## Overview
GB.Metasys.170815
METASYS N2 open
GOLD RX/PX/CX/SD, GENERATION E
Applicable to program version 1.10 and newer versions
Metasys N2 open |  |  |  | Metasys N2 open Virtual Objects
Metasys nodes contains up to 256 Virtual Objects. These virtual objects can be either one of seven region types; 1) Analog Input, 2) Binary Input, 3) Analog Output, 4) Binary Output, 5) Internal Float, 6) Internal Integer and 7) Internal Byte. The Metasys N2 Master performs read and write commands to these Virtual Objects and performs cyclic polling of all the virtual objects as well. |  |  |  | A virtual object contains data of a specific type. These types are called Regions. A Metasys N2 node may contain up to 256 Virtual Objects per region, which in all gives a total of 1792 virtual objects. In smaller systems it might be desirable to limit the number of virtual objects to reduce memory consumption. The regions are defined as followed.
Region | Type | Short | Description
Region 1 | Analog Input | AI | 32 bit, IEEE-standard floats.
Region 2 | Binary Input | BI | 1 bit
Region 3 | Analog Output | AO | 32 bit, IEEE-standard floats.
Region 4 | Binary Output | BO | 1 bit
Region 5 | Internal Float | IF | 32 bit, IEEE-standard floats.
Region 6 | Internal Integer | ADI | Signed 16 bit.
Region 7 | Internal Byte | IB | 8 bit.
The 7 regions of a Metasys Virtual Object. |  |  |  | A Metasys Node can contain up to 1792 Virtual Objects.
Virtual Object
Analog Input
Binary Input
Binary Output
Analog Output Output
Internal Float
Internal Integer
Internal Byte
Virtual Object
1
n
2

## Overview parameters
GB.Metasys.170815
Operation level |  | Adi,141 |  | EA AHU filter pressure level |  | Ai,19 |  | EA Temperature |  | Ai,46
Communication operation level |  | Adi,109 |  | EA AHU filter pressure alarm limit |  | Ai,20 |  | EA/Room temperature set point |  | Ao,71
Operation active |  | Bi,1 | [5 empty] | SA min temp set point |  | Ao,72
Low speed operation active |  | Bi,3 | [5 empty] | SA max temp set point |  | Ao,73
High speed operation active |  | Bi,4 |  |  | EA Duct pressure |  | Ai,7
Damper operation active |  | Bi,2 |  |  | EA low speed pressure set point |  | Ao,10
Triggered alarm #1 |  | Adi,144 |  |  | EA high speed pressure set point |  | Ao,12 | SA Duct pressure |  | Ai,5
A-alarm active |  | Bi,13 | [5 empty] | SA low speed pressure set point |  | Ao,9
B-alarm active |  | Bi,14 | [5 empty] | SA high speed pressure set point |  | Ao,11
Alarm reset |  | Bo,1
[8 empty] | SA Temperature |  | Ai,44
[8 empty] | SA temperature set point |  | Ao,70
EA Air flow |  | Ai,3 | [5 empty] | ERS 1 diff |  | Ao,60
EA Fan level |  | Ai,24
EA low speed air flow set point |  | Ao,2
EA high speed air flow set point |  | Ao,4
Outdoor temperature |  | Ai,49
SA AHU filter pressure level |  | Ai,17
SA AHU filter pressure alarm limit |  | Ai,18
Heat exchanger regulator level |  | Ai,63
RHX operation level |  | Ai,77
| SA Air flow |  | Ai,1 |  | Reheat regulator level |  | Ai,66 | Cool regulator level |  | Ai,73
| SA Fan level |  | Ai,23 |  | Re-heat output |  | Bi,38 | Cool output 1 |  | Bi,43
| SA low speed air flow set point |  | Ao,1 |  | Re-heat anti frost temp/overheat input |  | Ai,101 | Cool output 2 |  | Bi,44
| SA high speed air flow set point |  | Ao,3

## Binary Output
GB.Metasys.170815
Binary Output (BO).1bit (R/W).
N2 Idx | Name | Description | Min | Max | Unit | Default | Misc
Alarm settings
1 | Alarm reset | Resets all active alarms | 0 | 1 |  | 0
2
3 | Internal fire alarm function
4 | Internal fire alarm reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
5
6 |  |  | 0 | 1 |  | 0
7 | External fire alarm no. 1 reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
8 | External fire alarm no. 2 reset function | 0=manual reset, 1=auto reset
9
10
11 | External alarm no. 1 reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
12 | External alarm no. 2 reset function | 0=manual reset, 1=auto reset | 0 | 1 |  | 0
13
14
15 | External alarm no. 1 input function | 0=alarm at closed contact, 1=alarm at open contact | 0 | 1 |  | 0
16 | External alarm no. 2 input function | 0=alarm at closed contact, 1=alarm at open contact | 0 | 1 |  | 0
17
18
19
20
21
22
23
24
25
26
27
28
Pressure sensors zero point calibration
29 | SA flow pressure sensor auto zero calibration |  | 0 | 1 |  | 1
30 | EA flow pressure sensor auto zero calibration |  | 0 | 1 |  | 1
31 | SA duct pressure sensor auto zero calibration |  | 0 | 1 |  | 1
32 | EA duct pressure sensor auto zero calibration |  | 0 | 1 |  | 1
33 | ReCO2 pressure sensor auto zero calibration |  | 0 | 1 |  | 1
34 | RHX defrost pressure sensor auto calibration |  | 0 | 1 |  | 1
35 | Carry over control pressure sensor auto calibration |  | 0 | 1 |  | 1
36 | SA filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
37 | EA filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
38 | SA pre-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
39 | EA pre-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
40 | SA end-filter pressure sensor auto zero calibration |  | 0 | 1 |  | 1
41 | PX heat exchange pressure sensor auto calibration |  | 0 | 1 |  | 1 | 1.21
42
43
44
45
46 | SA flow pressure sensor activate zero calibration | If value is set to 1 for min 1s calibration will be performed. | 0 | 1 |  | 0
47 | EA flow pressure sensor activate zero calibration |  | 0 | 1 |  | 0
48 | SA duct pressure sensor activate zero calibration |  | 0 | 1 |  | 0
49 | EA duct pressure sensor activate zero calibration |  | 0 | 1 |  | 0
50 | ReCO2 pressure sensor activate calibration |  | 0 | 1 |  | 0
51 | RHX Defrost pressure sensor activate calibration |  | 0 | 1 |  | 0
52 | Carry over control pressure sensor activate zero calibration |  | 0 | 1 |  | 0
53 | SA filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
54 | EA filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
55 | SA pre-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
56 | EA pre-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
57 | SA end-filter pressure sensor activate zero calibration |  | 0 | 1 |  | 0
58 | PX heat exchange pressure sensor activate zero calibration |  | 0 | 1 |  | 1 | 1.21
59
60
61
62
AHU external sensors
63 | External room sensor 1 function |  | 0 | 1 |  | 0
64 | External room sensor 2 function |  | 0 | 1 |  | 0
65 | External room sensor 3 function |  | 0 | 1 |  | 0
66 | External room sensor 4 function |  | 0 | 1 |  | 0
67 | External room temp from BMS function |  | 0 | 1 |  | 0
68 | External OA sensor 1 function |  | 0 | 1 |  | 0
69 | External OA sensor 2 function |  | 0 | 1 |  | 0
70 | External OA sensor 3 function |  | 0 | 1 |  | 0
71 | External OA sensor 4 function |  | 0 | 1 |  | 0
72 | External OA temp from BMS function |  | 0 | 1 |  | 0
AHU Heat exchange
73 | RHX defrost function | Setting for activating the defrost function for the rotary heat exchanger. | 0 | 1 |  | 0
74 | RHX defrost calibration |  | 0 | 1 |  | 0
75 | RHX carry over control function | Setting for activating the carry over control function for the rotary heat exchanger. | 0 | 1 |  | 0
76 | RHX min exhaust air temp function |  | 0 | 1 |  | 0
77 | PHX periodic operation of bypass damper function |  | 0 | 1 |  | 1
78 | CHX periodic operation of pump function |  | 0 | 1 |  | 1
79 | CHX periodic operation of valve function |  | 0 | 1 |  | 1
AHU Heat/Cool
80 | Re-heat periodic operation of pump function |  | 0 | 1 |  | 1
81 | Re-heat periodic operation of valve function |  | 0 | 1 |  | 1
82 | Extra regulation sequence 1 output function | 0=0-10V, 1=10-0V | 0 | 1 |  | 0
83 | Extra regulation 1 periodic operation of pump function |  | 0 | 1 |  | 1
84 | Extra regulation 1 periodic operation of valve function |  | 0 | 1 |  | 1
85 | Extra regulation 1 temperature protection function |  | 0 | 1 |  | 0
86 | Season heat manual setting | 0=Re-heat, 1=Extra regulation sequence | 0 | 1 |  | 0
87 | Cool relay 1 periodic operation of pump function |  | 0 | 1 |  | 0
88 | Cool relay 2 periodic operation of pump function |  | 0 | 1 |  | 0
89 | Cool periodic operation of valve function |  | 0 | 1 |  | 0
Summer night cool/Intermittent night heat /Morning boost
90 | Summer night cool function |  | 0 | 1 |  | 0
91 | Intermittent night heat function |  | 0 | 1 |  | 0
92 | Morning boost function |  | 0 | 1 |  | 0
Cooling boost/heating boost
93 | Heating boost function |  | 0 | 1 |  | 0
Xzone function
94 | Xzone heat function |  | 0 | 1 |  | 0
95 | Xzone cool function |  | 0 | 1 |  | 0
Xzone external sensors
96 | Xzone external room sensor 1 function |  | 0 | 1 |  | 0
97 | Xzone external room sensor 2 function |  | 0 | 1 |  | 0
98 | Xzone external room sensor 3 function |  | 0 | 1 |  | 0
99 | Xzone external room sensor 4 function |  | 0 | 1 |  | 0
100 | Xzone external room temp from BMS function |  | 0 | 1 |  | 0
Xzone Heat/Cool
101 | Xzone reheat periodic operation of pump function |  | 0 | 1 |  | 1
102 | Xzone reheat periodic operation of valve function |  | 0 | 1 |  | 1
103 | Xzone Cool relay 1 periodic operation of pump function |  | 0 | 1 |  | 0
104 | Xzone Cool relay 2 periodic operation of pump function |  | 0 | 1 |  | 0
105 | Xzone Cool periodic operation of valve function |  | 0 | 1 |  | 0
Pre-heat
106 | Pre-heat function |  | 0 | 1 |  | 0
107 | Pre-heat periodic operation of pump function |  | 0 | 1 |  | 1
108 | Pre-heat periodic operation of valve function |  | 0 | 1 |  | 1
ReCO2
109 | ReCO2 Calibration |  | 0 | 1 |  | 0
Humidity/VOC
110 | Humidifying sensor | 0=SA, 1=EA | 0 | 1 |  | 0
111 | Dehumidifying function | Moved to Ii,165 | 0 | 1 |  | 1 | 1.12
112 | Heat exchange active in dehumidifying sequence |  | 0 | 1 |  | 0
113 | VOC sensor function | Moved to Ii,166 | 0 | 1 |  | 0 | 1.23
AYC
114 | AYC Heated water periodic operation of pump |  | 0 | 1 |  | 1
115 | AYC Heated water periodic operation of valve |  |  | 1 |  | 0
116 | AYC Heated water OA temp compensation |  | 0 | 1 |  | 0
117 | AYC Heated water room temp compensation function |  | 0 | 1 |  | 0
118 | AYC Heated water room temp compensation at night | 0=Enabled during night, 1=Disabled during night | 0 | 1 |  | 0
119 | AYC Heated water night temp compensation function |  | 0 | 1 |  | 0
120 | AYC Chilled water periodic operation of pump |  | 0 | 1 |  | 1
121 | AYC Chilled water periodic operation of valve |  |  | 1 |  | 0
122 | AYC Chilled water OA temp compensation |  | 0 | 1 |  | 0
123 | AYC Chilled water room temp compensation function |  | 0 | 1 |  | 0
124 | AYC Chilled water room temp compensation at night | 0=Enabled during night, 1=Disabled during night | 0 | 1 |  | 0
125 | AYC Chilled water night temp compensation function |  | 0 | 1 |  | 0
126 | AYC Chilled water dew point compensation air flow boost |  | 0 | 1 |  | 0
Optimize
127 | Optimize function |  | 0 | 1 |  | 0
128 | Intermittent night heat recirculation function |  | 0 | 1 |  | 1 | 1.12

## Binary Input
GB.Metasys.170815
Binary Input (BI).1bit (RO).
N2 Idx | Name | Description | Min | Max | Unit | Default | Misc
Operation level/alarm
1 | Operation active | Relay output status | 0 | 1
2 | Damper operation active | Relay output status | 0 | 1
3 | Low speed operation active | Low speed operation status | 0 | 1
4 | High speed operation active | High speed operation status | 0 | 1
5 | Intermittent night heat active |  | 0 | 1
6 | Morning boost active |  | 0 | 1
7 | Heating boost active |  | 0 | 1
8 | Cooling boost active |  | 0 | 1
9 | Summer night cool active |  | 0 | 1
10
11
12
13 | A-alarm active | Any alarm with priority class A active | 0 | 1
14 | B-alarm active | Any alarm with priority class B active | 0 | 1
15
16
Heat exchange
17 | HX operation active | HX status | 0 | 1
18 | HX cool recovery active | HX cool recovery status | 0 | 1
19 | HX defrost active | HX defrost status | 0 | 1
20
21
22 | RHX speed monitor signal | RHX speed monitor status | 0 | 1
23
24
25
26
27 | CHX-1 pump output | CHX-1 relay output status | 0 | 1
28 | CHX-1 pump input | CHX-1 digital input status | 0 | 1
29
30
AHU Coils
31 | Season heat, extra regulation sequence allowed |  | 0 | 1
32 | Season heat, re-heat allowed |  | 0 | 1
33 | Extra regulation sequence 1, output | Relay output status | 0 | 1
34 | Extra regulation sequence 1, power reduction active |  | 0 | 1
35 | Extra regulation sequence 1, anti-frost regulation active |  | 0 | 1
36
37
38 | Re-heat output | Relay output status | 0 | 1
39 | Re-heat power reduction active |  | 0 | 1
40 | Re-heat anti-frost regulation active |  | 0 | 1
41
42
43 | Cool output 1 | Relay output status | 0 | 1
44 | Cool output 2 | Relay output status | 0 | 1
45
46
47
48
49
50
Pre-heat
51 | Pre-heat output | Relay output status | 0 | 1
52 | Pre-heat power reduction active |  | 0 | 1
53 | Pre-heat anti-frost regulation active |  | 0 | 1
54
55
Xzone
56 | Xzone heat output | Relay output status | 0 | 1
57 | Xzone heat power reduction active
58 | Xzone heat anti-frost regulation active
59
60
61
62
63 | Xzone cool output 1 | Relay output status | 0 | 1
64 | Xzone cool output 2 | Relay output status | 0 | 1
65
66
67
68
69
70
71
72
73
74
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
AYC
99 | AYC heat pump output | Relay output status | 0 | 1
100 | AYC heat pump input | Digital input status | 0 | 1
101
102
103
104 | AYC cool pump output | Relay output status | 0 | 1
105 | AYC cool pump input | Digital input status | 0 | 1
106
107
108
COOL DX
109 | COOL DX compressor 1 output | Relay output status | 0 | 1
110 | COOL DX compressor 1 input | Digital input status | 0 | 1
111
112
113
114
115 | COOL DX compressor 2 output | Relay output status | 0 | 1
116 | COOL DX compressor 2 input | Digital input status | 0 | 1
117
118
119
120
Time schedule
121 | Effective period | 0=Inactive, 1=Active | 0 | 1
122 | Exception schedule 1 | 0=Inactive, 1=Active | 0 | 1
123 | Exception schedule 2 | 0=Inactive, 1=Active | 0 | 1
124 | Calendar 1 | 0=Inactive, 1=Active | 0 | 1
125 | Calendar 2 | 0=Inactive, 1=Active | 0 | 1
Alarms
151 | Active alarm group 1 |  | 0 | 1
152 | Active alarm group 2 |  | 0 | 1
153 | Active alarm group 3 |  | 0 | 1
154 | Active alarm group 4 |  | 0 | 1
155 | Active alarm group 5 |  | 0 | 1
156 | Active alarm group 6 |  | 0 | 1
157 | Active alarm group 7 |  | 0 | 1
158 | Active alarm group 8 |  | 0 | 1
159 | Active alarm group 9 |  | 0 | 1
160 | Active alarm group 10 |  | 0 | 1
161 | Active alarm group 11 |  | 0 | 1
162 | Active alarm group 12 |  | 0 | 1
163 | Active alarm group 13 |  | 0 | 1
164 | Active alarm group 14 |  | 0 | 1
165 | Active alarm group 15 |  | 0 | 1
166 | Active alarm group 16 |  | 0 | 1
167 | Active alarm group 17 |  | 0 | 1
168 | Active alarm group 18 |  | 0 | 1
169 | Active alarm group 19 |  | 0 | 1
170 | Active alarm group 20 |  | 0 | 1
171 | Active alarm group 21 |  | 0 | 1
172 | Active alarm group 22 |  | 0 | 1
173 | Active alarm group 23 |  | 0 | 1
174 | Active alarm group 24 |  | 0 | 1
175 | Active alarm group 25 |  | 0 | 1
176 | Active alarm group 26 |  | 0 | 1
177 | Active alarm group 27 |  | 0 | 1
178 | Active alarm group 28 |  | 0 | 1
179 | Active alarm group 29 |  | 0 | 1
180 | Active alarm group 30 |  | 0 | 1
181 | Active alarm group 31 |  | 0 | 1
182 | Active alarm group 32 |  | 0 | 1
183 | Active alarm group 33 |  | 0 | 1
184 | Active alarm group 34 |  | 0 | 1
185 | Active alarm group 35 |  | 0 | 1
186 | Active alarm group 36 |  | 0 | 1
187 | Active alarm group 37 |  | 0 | 1
188 | Active alarm group 38 |  | 0 | 1
189 | Active alarm group 39 |  | 0 | 1
190 | Active alarm group 40 |  | 0 | 1
191 | Active alarm group 41 |  | 0 | 1
192 | Active alarm group 42 |  | 0 | 1
193 | Active alarm group 43 |  | 0 | 1
194 | Active alarm group 44 |  | 0 | 1
195 | Active alarm group 45 |  | 0 | 1
196 | Active alarm group 46 |  | 0 | 1
197 | Active alarm group 47 |  | 0 | 1
198 | Active alarm group 48 |  | 0 | 1
199 | Active alarm group 49 |  | 0 | 1
200 | Active alarm group 50 |  | 0 | 1
201 | Active alarm group 51 |  | 0 | 1
202 | Active alarm group 52 |  | 0 | 1
203 | Active alarm group 53 |  | 0 | 1
204 | Active alarm group 54 |  | 0 | 1
205 | Active alarm group 55 |  | 0 | 1
206 | Active alarm group 56 |  | 0 | 1
207 | Active alarm group 57 |  | 0 | 1
208 | Active alarm group 58 |  | 0 | 1
209 | Active alarm group 59 |  | 0 | 1
210 | Active alarm group 60 |  | 0 | 1
211 | Active alarm group 61 |  | 0 | 1
212 | Active alarm group 62 |  | 0 | 1
213 | Active alarm group 63 |  | 0 | 1
214 | Active alarm group 64 |  | 0 | 1
215 | Active alarm group 65 |  | 0 | 1
216 | Active alarm group 66 |  | 0 | 1
217 | Active alarm group 67 |  | 0 | 1
218 | Active alarm group 68 |  | 0 | 1
219 | Active alarm group 69 |  | 0 | 1
220 | Active alarm group 70 |  | 0 | 1
221 | Active alarm group 71 |  | 0 | 1
222 | Active alarm group 72 |  | 0 | 1
223 | Active alarm group 73 |  | 0 | 1
224 | Active alarm group 74 |  | 0 | 1
225 | Active alarm group 75 |  | 0 | 1
226 | Active alarm group 76 |  | 0 | 1
227 | Active alarm group 77 |  | 0 | 1
228 | Active alarm group 78 |  | 0 | 1
229 | Active alarm group 79 |  | 0 | 1
230 | Active alarm group 80 |  | 0 | 1
231 | Active alarm group 81 |  | 0 | 1
232 | Active alarm group 82 |  | 0 | 1
233 | Active alarm group 83 |  | 0 | 1
234 | Active alarm group 84 |  | 0 | 1
235 | Active alarm group 85 |  | 0 | 1
236 | Active alarm group 86 |  | 0 | 1
237 | Active alarm group 87 |  | 0 | 1
238 | Active alarm group 88 |  | 0 | 1
239 | Active alarm group 89 |  | 0 | 1
240 | Active alarm group 90 |  | 0 | 1
241 | Active alarm group 91 |  | 0 | 1
242 | Active alarm group 92 |  | 0 | 1
243 | Active alarm group 93 |  | 0 | 1
244 | Active alarm group 94 |  | 0 | 1
245 | Active alarm group 95 |  | 0 | 1
246 | Active alarm group 96 |  | 0 | 1
247 | Active alarm group 97 |  | 0 | 1
248 | Active alarm group 98 |  | 0 | 1
249 | Active alarm group 99 |  | 0 | 1
250 | Active alarm group 100 |  | 0 | 1

## Analog Input
GB.Metasys.170815
Analog Input (AI).32 bit IEEE-standard floats (RO).
N2 Idx | Name | Description | Min | Max | Unit | Default | Misc
Air flow regulation
1 | SA Air flow | Present supply air flow. | 0 | 20000 | l/s
2 | SA Air flow regulator | Present supply air flow regulator set point. | 0 | 20000 | l/s
3 | EA Air flow | Present extract air flow. | 0 | 20000 | l/s
4 | EA Air flow regulator | Present extract air flow regulator set point. | 0 | 20000 | l/s
Pressure regulation
5 | SA Duct pressure | Present supply air duct pressure. | 0.0 | 2000.0 | Pa
6 | SA Duct pressure regulator | Present supply air duct pressure regulator set point. | 0.0 | 2000.0 | Pa
7 | EA Duct pressure | Present extract air duct pressure. | 0.0 | 2000.0 | Pa
8 | EA Duct pressure regulator | Present extract air duct pressure regulator set point. | 0.0 | 2000.0 | Pa
Demand regulation
9 | Demand input level | Present input signal for demand regulation. | 0.00 | 100.00 | %
10 | Demand regulator | Present demand regulator set point. | 0.00 | 100.00 | %
Air flow pressure sensors
11 | SA Air flow pressure | Present air flow pressure in the supply air fan inlet. | 0.0 | 2000.0 | Pa
12 | EA Air flow pressure | Present air flow pressure in the extract air fan inlet. | 0.0 | 2000.0 | Pa
Filters
13 | SA Pre-filter pressure level | Present supply air pre-filter pressure drop. | 0.0 | 2000.0 | Pa
14 | SA Pre-filter pressure alarm limit | Present supply air pre-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
15 | EA Pre-filter pressure level | Present extract air pre-filter pressure drop. | 0.0 | 2000.0 | Pa
16 | EA Pre-filter pressure alarm limit | Present extract air pre-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
17 | SA AHU filter pressure level | Present supply air filter pressure drop. | 0.0 | 2000.0 | Pa
18 | SA AHU filter pressure alarm limit | Present supply air filter pressure alarm limit. | 0.0 | 2000.0 | Pa
19 | EA AHU filter pressure level | Present extract air filter pressure drop. | 0.0 | 2000.0 | Pa
20 | EA AHU filter pressure alarm limit | Present extract air filter pressure alarm limit. | 0.0 | 2000.0 | Pa
21 | SA End-filter pressure level | Present supply air end-filter pressure drop. | 0.0 | 2000.0 | Pa
22 | SA End-filter pressure alarm limit | Present supply air end-filter pressure alarm limit. | 0.0 | 2000.0 | Pa
Fans
23 | SA Fan level | Present fan speed level of the supply air fan. | 0.00 | 100.00 | %
24 | EA Fan level | Present fan speed level of the extract air fan. | 0.00 | 100.00 | %
25 | SA Fan speed | Present fan speed level of the supply air fan. | 0 | 4000 | rpm
26 | EA Fan speed | Present fan speed level of the extract air fan. | 0 | 4000 | rpm
27 | SA Voltage | Present voltage level of the supply air fan. | 0 | 500 | V
28 | EA Voltage | Present voltage level of the extract air fan. | 0 | 500 | V
29 | SA Fan current | Present current level of the supply air fans. Includes all supply air fans. | 0 | 32.700 | A
30 | EA Fan current | Present current level of the extract air fans. Includes all supply air fans. | 0 | 32.700 | A
31 | SA Fan power | Present power level of the supply air fans. Includes all supply air fans. | 0 | 45.000 | kW
32 | EA Fan power | Present power consumption level of the extract air fans. Includes all extract air fans. | 0 | 45.000 | kW
33 | SA Fan kWh | Total power consumption of the supply air fans. Includes all supply air fans. | 0 | 9999 | kWh
34 | EA Fan kWh | Total power consumption level of the extract air fans. Includes all extract air fans. | 0 | 9999 | kWh
35 | SA Fan MWh | Total power consumption of the supply air fans. Includes all supply air fans. | 0 | 9999 | MWh
36 | EA Fan MWh | Total power consumption level of the extract air fans. Includes all extract air fans. | 0 | 9999 | MWh
37
38
39 | SA Fan min air flow | Supply air AHU min air flow | 0 | 18000 | l/s
40 | EA Fan min air flow | Extract air AHU min air flow | 0 | 18000 | l/s
41 | SA Fan max air flow | Supply air AHU max air flow | 0 | 18000 | l/s
42 | EA Fan max air flow | Extract air AHU max air flow | 0 | 18000 | l/s
43 | SFP | Calculated SFP level. | 0.0 | 1000.0 | kW/m3/s
AHU Temperature sensors
44 | SA Temperature | Present supply air temperature. | -55.00 | 125.00 | °C
45 | SA-D Temperature | Present supply air density temperature. | -55.00 | 125.00 | °C
46 | EA Temperature RX | Present extract air temperature in the unit (only AHU type RX). | -55.00 | 125.00 | °C
47 | EA-D Temperature | Present extract air density temperature. | -55.00 | 125.00 | °C
48 | EA Regulation temperature | Present extract air temperature used for regulation. | -55.00 | 125.00 | °C
49 | Outdoor temperature | Present outdoor air temperature in the unit. | -55.00 | 125.00 | °C
50 | Outdoor regulation temperature | Present outdoor air temperature used for regulation. | -55.00 | 125.00 | °C
51 | External outdoor temperature 1 | Present external outdoor temperature of sensor 1. | -55.00 | 125.00 | °C
52 | External outdoor temperature 2 | Present external outdoor temperature of sensor 2. | -55.00 | 125.00 | °C
53 | External outdoor temperature 3 | Present external outdoor temperature of sensor 3. | -55.00 | 125.00 | °C
54 | External outdoor temperature 4 | Present external outdoor temperature of sensor 4. | -55.00 | 125.00 | °C
55 | External outdoor temperature min/max/average | Present calculated min, max or average (depending of configuration) temperature of outd. sensor 1-4. | -55.00 | 125.00 | °C
56 | Room temperature 1 | Present room temperature of sensor 1. | -55.00 | 125.00 | °C
57 | Room temperature 2 | Present room temperature of sensor 2. | -55.00 | 125.00 | °C
58 | Room temperature 3 | Present room temperature of sensor 3. | -55.00 | 125.00 | °C
59 | Room temperature 4 | Present room temperature of sensor 4. | -55.00 | 125.00 | °C
60 | Room temperature min/max/average | Present calculated min, max or average (depending of configuration) temperature of room sensor 1-4. | -55.00 | 125.00 | °C
AHU Temperature regulation
61 | SA Temp regulator | Present supply air temperature regulator set point. | 0.00 | 50.00 | °C
62 | EA Temp regulator | Present extract air temperature regulator set point. | 0.00 | 50.00 | °C
63 | Heat recovery regulator level | Present operation level of the rotary heat exchanger. | 0.00 | 100.00 | %
64 | Extra regulation sequence 1 heat regulator level | Present level of extra regulation heat. | 0.00 | 100.00 | %
65 | Extra regulation sequence 1 heat output level |  | 0.00 | 100.00 | %
66 | Reheat regulator level | Present level of reheat. | 0.00 | 100.00 | %
67 | Reheat output level |  | 0.00 | 100.00 | %
68 | ReCO2 heat level | Present level of ReCO2 heat. | 0.00 | 100.00 | %
69 | Down regulation level | Present level of fan down regulation. | 0.00 | 100.00 | %
70 | Heating boost level | Present level of heating boost. | 0.00 | 100.00 | %
71 | Extra regulation sequence 1 cool regulator level | Present level of extra regulation cool. | 0.00 | 100.00 | %
72 | Extra regulation sequence 1 cool output level | Present level of extra regulation cool. | 0.00 | 100.00 | %
73 | Cool regulator level | Present level of cooling. | 0.00 | 100.00 | %
74 | Cool output level | Present level of cooling. | 0.00 | 100.00 | %
75 | ReCO2 cool level | Present level of ReCO2 heat. | 0.00 | 100.00 | %
76 | Cooling boost level | Present level of cooling boost. | 0.00 | 100.00 | %
AHU heat exchange
77 | RHX operation level | Present speed level of the rotary heat exchanger. | 0.00 | 100.00 | %
78 | RHX/PHX/CHX efficiency | Calculated level of the heat exchanger efficiency. | 0.00 | 100.00 | % |  | 1.23
79 | RHX defrost pressure level | Present pressure drop for the rotary heat exchanger. | 0.0 | 2000.0 | Pa
80 | RHX defrost pressure alarm limit | Present pressure drop alarm limit for the rotary heat exchanger. | 0.0 | 2000.0 | Pa
81 | RHX carry over control pressure level | Present pressure difference for the rotary heat exchangers purging sector. | 0.0 | 1000.0 | Pa
82
83 | PHX Bypass output | Present level of plate heat exchanger bypass output. | 0.00 | 100.00 | %
84 | PHX Bypass input | Present level of plate heat exchanger bypass input. | 0.00 | 100.00 | %
85 | PHX Bypass temperature 1 | Present bypass temperature sensor 1 in plate heat exchanger. | -55.00 | 125.00 | °C
86 | PHX Bypass temperature 2 | Present bypass temperature sensor 2 in plate heat exchanger. | -55.00 | 125.00 | °C
87 | CHX Valve output | Present level of coil heat exchanger valve output. | 0.00 | 100.00 | %
88 | CHX Valve input | Present level of coil heat exchanger valve input. | 0.00 | 100.00 | %
89 | CHX Return water temperature | Present return water temperature for coil heat exchanger. | -55.00 | 125.00 | °C
90
91
92
93
94
95 | PHX/CHX Humidity level | Present level of air-humidity for calculation of bypass/valve limitation. | 0.00 | 100.00 | %
96
97
98
AHU Coils
99 | Extra regulation sequence 1 anti frost temp/overheat input | Present extra regulation anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C
100 | Extra regulation sequence 1 input level |  | 0.00 | 100.00 | %
101 | Re-heat anti frost temp/overheat input | Present anti frost temperature for water heat coil. Value 0=overheat when electric heat is used. | -55.00 | 125.00 | °C
102 | Re-heat input level |  | 0.00 | 100.00 | %
103 | Cool water temperature | Present cool water temperature for water cool coil. | -55.00 | 125.00 | °C
104 | Cool input level |  | 0.00 | 100.00 | %
Xzone temperature sensors
105 | Xzone SA temperature | Present supply air temperature. | -55.00 | 125.00 | °C
106 | Xzone EA temperature | Present extract air temperature in the unit. | -55.00 | 125.00 | °C
107 | Xzone EA regulation temperature | Present extract air temperature used for regulation. | -55.00 | 125.00 | °C
108 | Xzone Room temperature 1 | Present room temperature of sensor 1. | -55.00 | 125.00 | °C
109 | Xzone Room temperature 2 | Present room temperature of sensor 2. | -55.00 | 125.00 | °C
110 | Xzone Room temperature 3 | Present room temperature of sensor 3. | -55.00 | 125.00 | °C
111 | Xzone Room temperature 4 | Present room temperature of sensor 4. | -55.00 | 125.00 | °C
112 | Xzone Room temperature min/max/average | Present calculated min, max or average (depending on configuration) temperature of room sensor 1-4. | -55.00 | 125.00 | °C
Xzone Temperature regulation
113 | Xzone SA Temp regulator | Present supply air temperature regulator set point. | 0.00 | 50.00 | °C
114 | Xzone EA Temp regulator | Present extract air temperature regulator set point. | 0.00 | 50.00 | °C
115 | Xzone re-heat regulator level |  | 0.00 | 100.00 | %
116 | Xzone cool regulator level |  | 0.00 | 100.00 | %
Xzone coils
117 | Xzone heat, anti frost temp/overheat input | Present Xzone heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C
118 | Xzone heat, output level | Present level of Xzone heat output. | 0 | 100.00 | %
119 | Xzone heat, input level | Present Xzone heat input. | 0 | 100.00 | %
120 | Xzone cool, water temperature |  | -55.00 | 125.00 | °C
121 | Xzone cool, output level | Present level of Xzone cool. | 0 | 100.00 | %
122 | Xzone cool, input level | Present Xzone cool valve position. | 0 | 100.00 | %
Pre-heat
123 | Pre-heat temperature | Present pre-heat temperature. | -55.00 | 125.00 | °C
124 | Pre-heat temp regulator set point | Present pre-heat temperature regulator set point. | -40.00 | 40.00 | °C
125 | Pre-heat temp regulator level |  | 0.00 | 100.00 | %
126 | Pre-heat anti frost temp/overheat input | Present pre-heat anti frost temperature for water heat coil. Value 0=Overheat when electric heat is used. | -55.00 | 125.00 | °C
127 | Pre-heat output level | Present pre-heat output level. | 0.00 | 100.00 | %
128 | Pre-heat input level | Present pre-heat input level. | 0.00 | 100.00 | %
ReCO2
129 | ReCO2 recirculation damper output | Present output signal to the recirculation damper. | 0.00 | 100.00 | %
130 | ReCO2 recirculation damper input | Present input signal from the recirculation damper. | 0.00 | 100.00 | %
131 | ReCO2 outdoor damper output | Present output signal to the outdoor air damper. | 0.00 | 100.00 | %
132 | ReCO2 outdoor damper input | Present input signal from the outdoor air damper. | 0.00 | 100.00 | %
133 | ReCO2 outdoor air flow | Present outdoor air flow level. | 0.0 | Ai,41 | l/s
134 | ReCO2 outdoor air flow regulator set point | Present outdoor air flow regulator set point. | 0.0 | Ai,41 | l/s
VOC
135 | VOC level | Present level of VOC | 450 | 10000 | ppm
COOL DX
136 | COOL DX, compressor 1 low pressure level |  | 0 | 34.50 | Bar
137 | COOL DX, compressor 1 high pressure level |  | 0 | 45.00 | Bar
138 | COOL DX, compressor 2 low pressure level |  | 0 | 34.50 | Bar
139 | COOL DX, compressor 2 high pressure level |  | 0 | 45.00 | Bar
AYC
140 | AYC Heat, heated water | Present heat temperature. | -55.00 | 125.00 | °C
141 | AYC Heat, heated water set point | Present heat temperature regulator set point. | 0 | 100.00 | °C
142 | AYC Heat, valve output | Present level of the heat valve output. | 0 | 100.00 | %
143 | AYC Heat, valve input | Present level of the heat valve input. | 0 | 100.00 | %
144 | AYC Heated water heat demand |  | 0 | 100.00 | %
145 | AYC Cool, chilled water | Present cool temperature. | -55.00 | 125.00 | °C
146 | AYC Cool, chilled water set point | Present cool temperature regulator set point. | 0 | 100.00 | °C
147 | AYC Cool, valve output | Present cool of the heat valve output. | 0 | 100.00 | %
148 | AYC Cool, valve input | Present cool of the heat valve input. | 0 | 100.00 | %
149 | AYC Chilled water cool demand |  | 0 | 100.00 | %
Software
150 | IQlogic software version | Present controller software version | 0.00 | 99.00
Humidity
151 | SA humidity level | Present level of supply air humidity | 0.00 | 100.00 | %RH
152 | SA humidity temperature | Present temperature inside the supply air humidity sensor. | -40.00 | 123.00 | °C
153 | SA dew point | Calculated supply air dew point. | -40.00 | 40.00 | °C
154 | EA humidity level | Present level of extract air humidity. | 0.00 | 100.00 | %RH
155 | EA humidity temperature | Present temperature inside the extract air humidity sensor. | -40.00 | 123.00 | °C
156 | EA dew point | Calculated extract air dew point. | -40.00 | 40.00 | °C
157
158 | Dehumidifying SA dew point regulator set point | Present supply air dew point regulator point. | -40.00 | 40.00 | °C
159 | Dehumidifying output level | Present level of the dehumidifying output. | 0.00 | 100.00 | %
160
161 | Humidifying SA regulator set point |  | 0.00 | 100.00 | %RH
162 | Humidifying output level | Present level of the humidifying output. | 0.00 | 100.00 | %
163
164
165
166
167
168
169
170 | EA duct temperature | Present extract air duct air temperature. | -55.00 | 125.00 | °C |  | 1.12
171
172

## Analog Output
GB.Metasys.170815
Analog Output (AO).32bit IEEE-standard floats (R/W).
N2 Idx | Name | Description | Min | Max | Unit | Default | Misc
Air flow regulation
1 | SA low speed air flow set point | Supply air flow set point for the unit when running in low speed operation. | 0 | Ao,3 | l/s
2 | EA low speed air flow set point | Extract air flow set point for the unit when running in low speed operation. | 0 | Ao,4 | l/s
3 | SA high speed air flow set point | Supply air flow set point for the unit when running in high speed operation. | Ao,1 | Ao,5 | l/s
4 | EA high speed air flow set point | Extract air flow set point for the unit when running in high speed operation. | Ao,2 | Ao,6 | l/s
5 | SA max speed air flow set point bost | Supply air flow max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | Ao,3 | Ai,41 | l/s
6 | EA max speed air flow set point bost | Extract air flow max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | Ao,4 | Ai,42 | l/s
7 | SA regulation zone | Supply air flow regulation zone setting in % of the present air flow set point that the regulator is allowed to work within. | 1.00 | 10.00 | % | 7.50
8 | EA regulation zone | Extract air flow regulation zone setting in % of the present air flow set point that the regulator is allowed to work within. | 1.00 | 10.00 | % | 7.50
Pressure regulation
9 | SA low speed pressure set point | Supply air duct pressure set point for the unit when running in low speed operation. | 0.0 | Ai,11 | Pa
10 | EA low speed pressure set point | Extract air duct pressure set point for the unit when running in low speed operation. | 0.0 | Ai,12 | Pa
11 | SA high speed pressure set point | Supply air duct pressure for the unit when running in high speed operation. | Ai,9 | Ai,13 | Pa
12 | EA high speed pressure set point | Extract air duct pressure set point for the unit when running in high speed operation. | Ai,10 | Ai,14 | Pa
13 | SA max speed pressure set point | Supply air duct pressure max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | Ai,11 | 750.0 | Pa
14 | EA max speed pressure set point | Extract air duct pressure max. limit for the unit when the low/high speed operation set point is altered by boosting function etc. | Ai,12 | 750.0 | Pa
15 | SA max speed output signal | Max. limit for the supply air fan speed when running in pressure regulation mode. | 0 | 100.00 | %
16 | EA max speed output signal | Max. limit for the extract air fan speed when running in pressure regulation mode. | 0 | 100.00 | %
17 | SA pressure regulation zone | Supply air pressure regulation zone setting in % of the present duct pressure set point that the regulator is allowed to work within. | 0 | 10.00 | % | 7.50
18 | EA pressure regulation zone | Extract air pressure regulation zone setting in % of the present duct pressure set point that the regulator is allowed to work within. | 0 | 10.00 | % | 7.50
Demand regulation
19 | Demand low speed demand set point | Set point for the 0..10V input signal for the unit when running in low speed operation. | 0.00 | 100.00 | % | 50.00
20 | Demand high speed demand set point | Set point for the 0..10V input signal for the unit when running in high speed operation. | 10.00 | 100.00 | % | 25.00
21 | SA min speed air flow set point | Supply air flow min. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | Ai,39 | Ao,23 | l/s
22 | EA min speed air flow set point | Extract air flow min. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | Ai,40 | Ao,24 | l/s
23 | SA max speed air flow set point demand | Supply air flow max limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | Ao,21 | Ai,41 | l/s
24 | EA max speed air flow set point demand | Extract air flow max. limit for the unit when the low/high speed operation set point is altered when running in fan regulation mode demand. | Ao,22 | Ai,42 | l/s
25 | SA demand P-band | Supply air demand regulator P-band setting. | 1.00 | 100.00 | % | 40.00
Slave controlled regulation
26 | Slave offset factor |  | 50.00 | 200.00 | % | 0.00
Fans OA temp compensation
27 | Outdoor temp compensation X1 |  | -50.00 | Ao,28 | °C | -20.00
28 | Outdoor temp compensation X2 |  | Ao,27 | Ao,29 | °C | -10.00
29 | Outdoor temp compensation X3 |  | Ao,28 | Ao,30 | °C | 10.00
30 | Outdoor temp compensation X4 |  | Ao,29 | 50.00 | °C | 20.00
31 | Outdoor temp compensation Y1 SA air flow |  | Ai,39 | Ai,41 | l/s
32 | Outdoor temp compensation Y2 SA air flow |  | Ai,39 | Ai,41 | l/s
33 | Outdoor temp compensation Y3 SA air flow |  | Ai,39 | Ai,41 | l/s
34 | Outdoor temp compensation Y4 SA air flow |  | Ai,39 | Ai,41 | l/s
35 | Outdoor temp compensation Y1 EA air flow |  | Ai,40 | Ai,42 | l/s
36 | Outdoor temp compensation Y2 EA air flow |  | Ai,40 | Ai,42 | l/s
37 | Outdoor temp compensation Y3 EA air flow |  | Ai,40 | Ai,42 | l/s
38 | Outdoor temp compensation Y4 EA air flow |  | Ai,40 | Ai,42 | l/s
39 | Outdoor temp compensation Y1 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
40 | Outdoor temp compensation Y2 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
41 | Outdoor temp compensation Y3 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
42 | Outdoor temp compensation Y4 SA pressure |  | 20.0 | 750.0 | Pa | 100.0
43 | Outdoor temp compensation Y1 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
44 | Outdoor temp compensation Y2 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
45 | Outdoor temp compensation Y3 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
46 | Outdoor temp compensation Y4 EA pressure |  | 20.0 | 750.0 | Pa | 100.0
Fans down regulation
47 | Down regulation neutralzone |  | 0.00 | 10.00 | K | 0.00
48 | Down regulation P-band |  | 1.00 | 10.00 | K | 5.00
Fans in operation at active fire alarm
49 | SA fan speed at fire alarm 1 |  | 0.00 | 100.00 | % | 100.00
50 | EA fan speed at fire alarm 1 |  | 0.00 | 100.00 | % | 100.00
51 | SA fan speed at fire alarm 2 |  | 10.00 | 100.00 | % | 100.00
52 | EA fan speed at fire alarm 2 |  | 10.00 | 100.00 | % | 100.00
53 | SA fan speed at internal fire alarm |  | 10.00 | 100.00 | % | 100.00
54 | EA fan speed at internal fire alarm |  | 10.00 | 100.00 | % | 100.00
Filters
55 | SA pre-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
56 | EA pre-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
57 | SA AHU-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
58 | EA AHU-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
59 | SA end-filter alarm limit |  | 30.0 | 500.0 | Pa | 100.0
ERS-1 reg.
60 | ERS 1 diff | Supply air temp difference setting according to the diagram for ERS 1. | 1.00 | 7.00 | K | 2.00
61 | ERS 1 breakpoint | Breakpoint temp setting according to the diagram for ERS 1. | 12.00 | 26.00 | °C | 22.00
ERS-2 reg.
62 | ERS 2 breakpoint X1 | Breakpoint X1 setting according to the diagram for ERS 2. | 10.00 | Ao,63 | °C | 15.00
63 | ERS 2 breakpoint X2 | Breakpoint X2 setting according to the diagram for ERS 2. | Ao,62 | Ao,64 | °C | 20.00
64 | ERS 2 breakpoint X3 | Breakpoint X3 setting according to the diagram for ERS 2. | Ao,63 | Ao,65 | °C | 22.00
65 | ERS 2 breakpoint X4 | Breakpoint X4 setting according to the diagram for ERS 2. | Ao,64 | 40.00 | °C | 24.00
66 | ERS 2 breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 20.00
67 | ERS 2 breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 18.00
68 | ERS 2 breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 14.00
69 | ERS 2 breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 12.00
SA Reg.
70 | SA temperature set point | Supply air temperature setting, for supply air temp regulation mode. | 10.00 | 40.00 | °C | 21.00
EA Reg.
71 | EA/Room temperature set point | Extract air/room temperature setting, for Extract air/room temp regulation mode. | 10.00 | 40.00 | °C | 21.00
72 | SA min temp set point | Supply air min. set point during EA/room regulation mode. | 8.00 | 30.00 | °C | 16.00
73 | SA max temp set point | Supply air max. set point during EA/room regulation mode. | 16.00 | 50.00 | °C | 28.00
74 | EA regultaion P-band |  | 1.00 | 10.00 | K | 5.00
ORS Reg.
75 | ORS breakpoint X1 | Breakpoint X1 setting according to the diagram for ORS. | -5.00 | Ao,76 | °C | -20.00
76 | ORS breakpoint X2 | Breakpoint X2 setting according to the diagram for ORS. | Ao,75 | Ao,77 | °C | -10.00
77 | ORS breakpoint X3 | Breakpoint X3 setting according to the diagram for ORS. | Ao,76 | Ao,78 | °C | 10.00
78 | ORS breakpoint X4 | Breakpoint X4 setting according to the diagram for ORS. | Ao,77 | 50.00 | °C | 20.00
79 | ORS breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
80 | ORS breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
81 | ORS breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
82 | ORS breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
ORE Reg.
83 | ORE breakpoint X1 | Breakpoint X1 setting according to the diagram for ORE. | -5.00 | Ao,84 | °C | -20.00
84 | ORE breakpoint X2 | Breakpoint X2 setting according to the diagram for ORE. | Ao,83 | Ao,85 | °C | -10.00
85 | ORE breakpoint X3 | Breakpoint X3 setting according to the diagram for ORE. | Ao,84 | Ao,86 | °C | 10.00
86 | ORE breakpoint X4 | Breakpoint X4 setting according to the diagram for ORE. | Ao,85 | 50.00 | °C | 20.00
87 | ORE breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
88 | ORE breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
89 | ORE breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
90 | ORE breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
AHU external sensors
91 | External room temp from BMS |  | -55.00 | 125.00 | °C | 0.00
92 | External OA temp from BMS |  | -55.00 | 125.00 | °C | 0.00
AHU Heat exchange
93 | RHX defrost start limit |  | 30.0 | 100.0 | Pa | 50.0
94 | RHX min exhaust air temp set point |  | -40.00 | 20.00 | °C | 5.00
95 | RHX min exhaust air temp P-band |  | 1.00 | 40.00 | K | 8.00
96 | PHX/CHX Bypass defrost limit | PHX is default 3°C, CHX is default 5°C. | -10.00 | 5.00 | °C
97 | PHX/CHX Bypass defrost P-band |  | 1.00 | 40.00 | K | 20.00
98 | Heat exchange temperature regulation P-band |  | 1.00 | 10.00 | K | 6.00
AHU Heat/Cool
99 | Re-heat P-band |  | 1.00 | 10.00 | K | 8.00
100 | Extra regulation sequence 1 heat max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00
101 | Extra regulation sequence 1 cool max output signal | Maximum output signal setting for the extra regulation sequence. | 0.00 | 100.00 | % | 100.00
102 | Extra regulation sequence 1 heat P-band |  | 1.00 | 10.00 | K | 8
103 | Extra regulation sequence 1 cool P-band |  | 1.00 | 10.00 | K | 6
104 | Extra regulation 1 temperature protection temperature |  | -50.00 | 100.00 | °C | 0.00
105 | Cool SA neutral zone |  | 0.50 | 10.00 | K | 2.00
106 | Cool EA neutral zone |  | 0.50 | 10.00 | K | 2.00
107 | Cool outdoor temp limit 1 |  | 0.00 | 30.00 | °C | 15.00
108 | Cool outdoor temp limit 2 |  | 0.00 | 30.00 | °C | 18.00
109 | Cool outdoor temp limit 3 |  | 0.00 | 30.00 | °C | 20.00
110 | Cool min supply air flow limit |  | 0 | Ai,41 | l/s
111 | Cool min extract air flow limit |  | 0 | Ai,42 | l/s
112 | Cool P-band |  | 1.00 | 10.00 | K | 6
Summer night cool/Intermittent night heat /Morning boost
113 | Summer night cool OA temp start limit |  | -5.00 | 15.00 | °C | 10.00
114 | Summer night cool EA temp start limit |  | 17.00 | 27.00 | °C | 22.00
115 | Summer night cool EA temp stop limit |  | 12.00 | 22.00 | °C | 16.00
116 | Summer night cool SA temp set point |  | 0.00 | 20.00 | °C | 10.00
117 | Intermittent night heat SA flow set point |  | Ai,39 | Ai,41 | l/s
118 | Intermittent night heat SA duct pressure set point |  | 20 | 750 | Pa | 100
119 | Intermittent night heat EA temp start limit |  | 5.00 | Ao,200 | °C | 16.00
120 | Intermittent night heat EA temp stop limit |  | Ao,119 | 25.00 | °C | 18.00
121 | Intermittent night heat SA temp set point |  | 5.00 | 50.00 | °C | 28.00
122 | Morning boost air flow set point |  | Ai,39 | Ai,41 | l/s
123 | Morning boost duct pressure set point |  | 20 | 750 | Pa | 100
Cooling boost/heating boost
124 | Cooling boost comfort start limit |  | 2.00 | 10.00 | K | 3.00
125 | Cooling boost comfort regulation speed |  | 1 | 25 | %/s | 4
126 | Cooling boost economy P-band |  | 1 | 10.00 | K
127 | Heating boost comfort start limit |  | 2.00 | 10.00 | K | 3.00
128 | Heating boost comfort regulation speed |  | 1 | 25 | %/s | 4
Xzone ERS-1 reg.
129 | Xzone ERS 1 diff | Supply air temp differental setting according to the diagram for ERS 1. | 1 | 7.00 | K | 2.00
130 | Xzone ERS 1 breakpoint | Breakpoint temp setting according to the diagram for ERS 1. | 12.00 | 26.00 | °C | 22.00
Xzone ERS-2 reg.
131 | Xzone ERS 2 breakpoint X1 | Breakpoint X1 setting according to the diagram for ERS 2. | 10 | Ao,132 | °C | 15.00
132 | Xzone ERS 2 breakpoint X2 | Breakpoint X2 setting according to the diagram for ERS 2. | Ao,131 | Ao,133 | °C | 20.00
133 | Xzone ERS 2 breakpoint X3 | Breakpoint X3 setting according to the diagram for ERS 2. | Ao,132 | Ao,134 | °C | 22.00
134 | Xzone ERS 2 breakpoint X4 | Breakpoint X4 setting according to the diagram for ERS 2. | Ao,133 | 40.00 | °C | 24.00
135 | Xzone ERS 2 breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 20.00
136 | Xzone ERS 2 breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 18.00
137 | Xzone ERS 2 breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 14.00
138 | Xzone ERS 2 breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ERS 2. | 10.00 | 40.00 | °C | 12.00
Xzone SA Reg.
139 | Xzone SA temperature set point | Supply air temperature setting, for supply air temp regulation mode. | 10.00 | 40.00 | °C | 21.00
Xzone EA Reg.
140 | Xzone EA/Room temperature set point | Extract air/room temperature setting, for Extract air/room temp regulation mode. | 10.00 | 40.00 | °C | 21.00
141 | Xzone SA min temp set point | Supply air min. set point during EA/room regulation mode. | 8.00 | 20.00 | °C | 16.00
142 | Xzone SA max temp set point | Supply air max. set point during EA/room regulation mode. | 16.00 | 50.00 | °C | 28.00
143 | Xzone EA regultaion P-band |  | 1.00 | 10.00 | K | 5.00
Xzone ORS Reg.
144 | Xzone ORS breakpoint X1 | Breakpoint X1 setting according to the diagram for ORS. | -5.00 | Ao,145 | °C | -20.00
145 | Xzone ORS breakpoint X2 | Breakpoint X2 setting according to the diagram for ORS. | Ao,144 | Ao,146 | °C | -10.00
146 | Xzone ORS breakpoint X3 | Breakpoint X3 setting according to the diagram for ORS. | Ao,145 | Ao,147 | °C | 10.00
147 | Xzone ORS breakpoint X4 | Breakpoint X4 setting according to the diagram for ORS. | Ao,146 | 50.00 | °C | 20.00
148 | Xzone ORS breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
149 | Xzone ORS breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
150 | Xzone ORS breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
151 | Xzone ORS breakpoint Y4 | Breakpoint Y4 setting according to the diagram for ORS. | 10.00 | 40.00 | °C | 21.50
Xzone ORE Reg.
152 | Xzone ORE breakpoint X1 | Breakpoint X1 setting according to the diagram for ORE. | -5.00 | Ao,153 | °C | -20.00
153 | Xzone ORE breakpoint X2 | Breakpoint X2 setting according to the diagram for ORE. | Ao,152 | Ao,154 | °C | -10.00
154 | Xzone ORE breakpoint X3 | Breakpoint X3 setting according to the diagram for ORE. | Ao,153 | Ao,155 | °C | 10.00
155 | Xzone ORE breakpoint X4 | Breakpoint X4 setting according to the diagram for ORE. | Ao,154 | 50.00 | °C | 20.00
156 | Xzone ORE breakpoint Y1 | Breakpoint Y1 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
157 | Xzone ORE breakpoint Y2 | Breakpoint Y2 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
158 | Xzone ORE breakpoint Y3 | Breakpoint Y3 setting according to the diagram for ORE. | 10.00 | 40.00 | °C | 21.50
159 | Xzone ORE breakpoint Y4 |  | 10.00 | 40.00 | °C | 21.50
Xzone external sensors
160 | Xzone external room temp from BMS |  | -55.00 | 125.00 | °C | 0.00
Xzone Heat/Cool
161 | Xzone reheat P-band |  | 1.00 | 10.00 | K | 8.00
162 | Xzone Cool SA neutral zone |  | 0.50 | 10.00 | K | 2.00
163 | Xzone Cool EA neutral zone |  | 0.50 | 10.00 | K | 2.00
164 | Xzone Cool P-band |  | 1.00 | 10.00 | K | 6.00
Pre-heat
165 | Pre-heat temperature set point |  | -40.00 | 40.00 | °C | 5.00
166 | Pre-heat P-band |  | 1.00 | 10.00 | K | 8.00
ReCO2
167 | ReCO2-CO2 set point |  | 0.00 | 100.00 | % | 50.00
168 | ReCO2 min. outdoor air |  | 0 | Ai,41 | l/s
169 | ReCO2 min. exhaust air |  | 0 | Ai,42 | l/s
170 | ReCO2-CO2 P-band |  | 1.00 | 100.00 | % | 50.00
171 | ReCO2-CO2 air flow boost reg. P-band |  | 10.00 | 100.00 | % | 50.00
172 | ReCO2 heat P-band |  | 1.00 | 10.00 | K | 7.00
173 | ReCO2 cool P-band |  | 1.00 | 10.00 | K | 6.00
Humidity/VOC
174 | Humidifying on/off start level |  | 10.00 | Ao,175 | %RH | 40.00
175 | Humidifying on/off stop level |  | Ao,174 | 95.00 | %RH | 45.00
176 | Humidifying 0-10V set point |  | 10.00 | 95.00 | %RH | 30.00
177 | Humidifying 0-10V SA max set point |  | 10.00 | 95.00 | %RH | 80.00
178 | Humidifying 0-10V SA P-band |  | 1.00 | 80.00 | %RH | 60.00
179 | Humidifying 0-10V EA P-band |  | 1.00 | 80.00 | %RH | 60.00
180 | Dehumidifying set point |  | 10.00 | 90.00 | %RH | 50.00
COOL DX
181 | COOL DX Low pressure stop limit |  | 1.00 | 10.00 | Bar | 3.00
182 | COOL DX High pressure stop limit |  | 25.00 | 40.00 | Bar | 39.00
AYC
183 | AYC Heated water temp set point |  | 10.00 | 80.00 | °C | 30.00
184 | AYC Heated water OA temp for start of pump |  | -40.00 | 40.00 |  | 15.00
185 | AYC Heated water OA temp for stop of pump |  | -40.00 | 40.00 |  | 18.00
186 | AYC Heated water OA temp compensation X1 |  | -40.00 | Ao,187 | °C | -20.00
187 | AYC Heated water OA temp compensation X2 |  | Ao,186 | Ao,188 | °C | 0.00
188 | AYC Heated water OA temp compensation X3 |  | Ao,187 | Ao,189 | °C | 5.00
189 | AYC Heated water OA temp compensation X4 |  | Ao,188 | 40.00 | °C | 15.00
190 | AYC Heated water OA temp compensation Y1 |  | -40.00 | 40.00 | °C | 40.00
191 | AYC Heated water OA temp compensation Y2 |  | -40.00 | 40.00 | °C | 30.00
192 | AYC Heated water OA temp compensation Y3 |  | -40.00 | 40.00 | °C | 20.00
193 | AYC Heated water OA temp compensation Y4 |  | -40.00 | 40.00 | °C | 15.00
194 | AYC Heated water room temp compensation temperature |  | 0.00 | 40.00 | °C | 21.00
195 | AYC Heated water room temp compensation P-band |  | 1.00 | 10.00 | K | 5.00
196 | AYC Heated water night temp compensation temp |  | -10.00 | 10.00 | K | -2.00
197 | AYC Heated water P-band |  | 1.00 | 40..00 | K | 15.00
198 | AYC Chilled water temp set point |  | 10.00 | 80.00 | °C | 30.00
199 | AYC Chilled water OA temp for start of pump |  | -40.00 | 40.00 |  | 15.00
200 | AYC Chilled water OA temp for stop of pump |  | -40.00 | 40.00 |  | 18.00
201 | AYC Chilled water OA temp compensation X1 |  | -40.00 | Ao,202 | °C | -20.00
202 | AYC Chilled water OA temp compensation X2 |  | Ao,201 | Ao,203 | °C | 0.00
203 | AYC Chilled water OA temp compensation X3 |  | Ao,202 | Ao,204 | °C | 5.00
204 | AYC Chilled water OA temp compensation X4 |  | Ao,203 | 40.00 | °C | 15.00
205 | AYC Chilled water OA temp compensation Y1 |  | -40.00 | 40.00 | °C | 40.00
206 | AYC Chilled water OA temp compensation Y2 |  | -40.00 | 40.00 | °C | 30.00
207 | AYC Chilled water OA temp compensation Y3 |  | -40.00 | 40.00 | °C | 20.00
208 | AYC Chilled water OA temp compensation Y4 |  | -40.00 | 40.00 | °C | 15.00
209 | AYC Chilledwater room temp compensation temperature |  | 0.00 | 40.00 | °C | 21.00
210 | AYC Chilled water room temp compensation P-band |  | 1.00 | 10.00 | K | 5.00
211 | AYC Chilled water night temp compensation temp |  | -10.00 | 10.00 | K | -2.00
212 | AYC Chilled water dew point compensation neutral zone |  | 0 | 5.00 | K | 2.00
213 | AYC Chilled water dew point compensation regulation speed | Percent air flow boost of each increased chilled water set point. | 0 | 30.00 | %/K | 10.00
214 | AYC Chilled water P-band |  | 1.00 | 40..00 | K | 15.00
Optimize
215 | Optimize SA pressure set point |  | 20.0 | 750.0 | Pa | 0
216 | Optimize EA pressure set point |  | 20.0 | 750.0 | Pa | 0
MISC
217 | Cool exchange temperature regulation P-band |  | 1.00 | 10.00 | K | 6.00 | 1.11
218 | Intermittent night heat EA flow set point |  | Ai,40 | Ai,42 | l/s |  | 1.12
219 | Intermittent night heat EA duct pressure set point |  | 20 | 750 | Pa |  | 1.12
220 | Summer night cool SA flow set point |  | Ai,39 | Ai,41 | l/s |  | 1.22
221 | Summer night cool EA flow set point |  | Ai,40 | Ai,42 | l/s |  | 1.22
222 | Summer night cool SA duct pressure set point |  | 20 | 750 | Pa | 100 | 1.22
223 | Summer night cool EA duct pressure set point |  | 20 | 750 | Pa | 100 | 1.22

## Int Integer
GB.Metasys.170815
Internal Integer (ADI).Signed 16bit(RW 1-116, RO 117-163)
N2 Idx | Name | Description | Min | Max | Unit | Default | Misc
AHU fan regulation
1 | SA Fan regulation mode | Setting of regulation type for the supply air fan. 0=Air flow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by EA fan | 0 | 3 |  | 0
2 | EA Fan regulation mode | Setting of regulation type for the extract air fan. 0=Air flow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by SA fan | 0 | 3 |  | 0
Air flow regulation
3 | SA regulation I-time | Supply air flow regulator affection setting. | 1 | 1800 | s | 30
4 | EA regulation I-time | Extract air flow regulator affection setting. | 1 | 1800 | s | 30
Pressure regulation
5 | SA pressure I-time | Supply air pressure regulator affection setting. | 0 | 1800 | s | 30
6 | EA pressure I-time | Extract air pressure regulator affection setting. | 0 | 1800 | s | 30
Demand regulation
7 | SA demand I-time | Supply air demand regulator affection setting. | 1 | 1800 | s | 1200
Fans OA temp compensation
8 | Outdoor temp compensation function | 0=Inactive, 1=Active at low speed, 2=Active at high speed, 3=Active at low and high speed. | 0 | 3 |  | 0
Fans down regulation
9 | Down regulation function | 0=Inactive, 1=SA, 2=SA and EA | 0 | 2 |  | 1
10 | Down regulation I-time |  | 1 | 1800 | s | 30
Fans in operation at active fire alarm
11 | Fans in operation at fire alarm 1 function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3
12 | Fans in operation at fire alarm 2 function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3
13 | Fans in operation at internal fire alarm function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3
Filters
14 | Pre-filter function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3 |  | 0
15 | Pre-filter calibration | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3 |  | 0
16 | AHU filter function | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3
17 | AHU filter calibration | 0=Inactive, 1=SA, 2=EA, 3=SA and EA | 0 | 3 |  | 0
AHU Temperature regulation
18 | Temperature regulation mode | 1=ERS-1, 2=ERS-2, 3=SA, 4=EA, 5=ORS, 6=ORE | 1 | 6 |  | 3
ERS-1 reg.
19 | ERS 1 step | Curve setting according to the diagram for ERS 1. | 1 | 4 |  | 2
EA Reg.
20 | EA regultaion I-time |  | 1 | 1800 | s | 30
AHU external sensors
21 | External room sensors measurement function | 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
22 | External room temp from BMS alarm time |  | 0 | 9999 | min | 5
23 | External OA sensors measurement function | 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
24 | External OA temp from BMS alarm time |  | 0 | 9999 | min | 5
AHU Heat exchange
25 | PHX periodic operation interval |  | 0 | 168 | h | 24
26 | PHX periodic operation time |  | 0 | 60 | min | 3
27 | CHX periodic operation interval |  | 0 | 168 | h | 24
28 | CHX periodic operation time |  | 0 | 60 | min | 3
29 | PHX/CHX Bypass defrost I-time |  | 1 | 600 | s | 60
30 | Heat exchange temperature regulation I-time |  | 1 | 1800 | s | 50
AHU Heat/Cool
31 | Re-heat I-time |  | 1 | 1800 | s | 70
32 | Re-heat periodic operation interval |  | 0 | 168 | h | 24
33 | Re-heat periodic operation time |  | 0 | 60 | min | 3
34 | Extra regulation sequence 1 function | 0=Inactive, 1=Heat, 2=Cool, 3=Heat and Cool. | 0 | 3 |  | 0
35 | Extra regulation sequence 1 heat I-time |  | 1 | 1800 | s | 70
36 | Extra regulation sequence 1 cool I-time |  | 1 | 1800 | s | 60
37 | Extra regulation 1 periodic operation interval |  | 0 | 168 | h | 24
38 | Extra regulation 1 periodic operation time |  | 0 | 60 | min | 3
39 | Extra regulation 1 temperature protection alarm delay |  | 0 | 9999 | min | 5
40 | Season heat function | 0=Inactive, 1=Extra regulation sequence at closed input, 2=Extra regulation sequence at open input, 3=Manual mode. | 0 | 3 |  | 0
41 | Cool on/off regulation function | 0=Inactive, 1=1 step, 2=2 steps, 3=3 steps. | 0 | 3 |  | 0
42 | Cool restart time | Setting of cool restart time between start-start. | 0 | 15 | min | 5
43 | Cool step up delay time | Setting of on/off cooling and COOL DX time delay between steps. | 0 | 10 | min | 5
44 | Cool stand still time | Setting of on/off cooling and COOL DX time delay before stop-start | 0 | 20 | min | 5
45 | Cool I-time |  | 1 | 1800 | s | 60
46 | Cool periodic operation interval |  | 0 | 168 | h | 24
47 | Cool periodic operation time |  | 0 | 60 | min | 3
Summer night cool/Intermittent night heat /Morning boost
48 | Summer night cool start time (hour) |  | 0 | 23 | h | 23
49 | Summer night cool start time (minute) |  | 0 | 59 | min | 0
50 | Summer night cool stop time (hour) |  | 0 | 23 | h | 23
51 | Summer night cool stop time (minute) |  | 0 | 59 | min | 0
52 | Morning boost start time (hour) |  | 0 | 23 | h | 0
53 | Morning boost start time (minute) |  | 0 | 59 | min | 0
Cooling boost/heating boost
54 | Cooling boost function | 0=Inactive, 1=Comfort, 2=Economy, 3=Sequence, 4=Comfort and Economy, 5=Economy and Sequence | 0 | 5 |  | 0
55 | Cooling boost economy I-time |  | 1 | 1800 | s
Xzone temperature regulation
56 | Xzone temperature regulation mode | 1=ERS-1, 2=ERS-2, 3=SA, 4=EA, 5=ORS, 6=ORE | 1 | 6 |  | 1
Xzone ERS-1 reg.
57 | Xzone ERS 1 step | Curve setting according to the diagram for ERS 1. | 1 | 4
Xzone EA Reg.
58 | Xzone EA regultaion I-time |  | 1 | 1800 | s | 180
Xzone external sensors
59 | Xzone external room sensors measurement function | 0=Average, 1=Min, 2=Max | 0 | 2 |  | 0
60 | Xzone external room temp from BMS alarm time |  | 0 | 9999 | min | 5
Xzone Heat/Cool
61 | Xzone reheat I-time |  | 1 | 1800 | s | 70
62 | Xzone reheat periodic operation interval |  | 0 | 168 | h | 24
63 | Xzone reheat periodic operation time |  | 0 | 60 | min | 3
64 | Xzone Cool on/off regulation function | 0=Inactive, 1=1 step, 2=2 steps, 3=3 steps. | 0 | 3 |  | 0
65 | Xzone Cool I-time |  | 1 | 1800 | s | 60
66 | Xzone Cool periodic operation interval |  | 0 | 168 | h | 24
67 | Xzone Cool periodic operation time |  | 0 | 60 | min | 3
Pre-heat
68 | Pre-heat I-time |  | 1 | 1800 | s | 70
ReCO2
69 | ReCO2-CO2 function | 0=Inactive, 1=CO2, 2=CO2 and air flow boost | 0 | 2 |  | 0
70 | ReCO2 temperature regulation sequence function | 0=Inactive, 1=Heat, 2=Cool, 3=Heat and Cool. | 0 | 3 |  | 0
71 | ReCO2-CO2 I-time |  | 1 | 1800 | s | 60
72 | ReCO2-CO2 air flow boost reg. I-time |  | 1 | 1800 | s | 60
73 | ReCO2 heat I-time |  | 1 | 1800 | s | 70
74 | ReCO2 cool I-time |  | 1 | 1800 | s | 60
Humidity/VOC
75 | Humidifying function | 0=Inactive, 1=on/off, 2=0-10V | 0 | 2 |  | 0
76 | Humidifying 0-10V SA I-time |  | 1 | 1800 | s | 30
77 | Humidifying 0-10V EA I-time |  | 1 | 1800 | s | 180
COOL DX
78 | COOL DX Function | 0=Inactive, 1=Economy, 2=Comfort, 3=Top | 0 | 3 |  | 0
79 | COOL DX Restart time | Time setting between start - start | 5 | 15 | min | 5
AYC
80 | AYC Function | 0=Inactive, 1=Chilled water, 2=Heated water, 3=Chilled and heated water | 0 | 3 |  | 0
81 | AYC Heated water alarm function for pump | 0=Inactive, 1= Alarm at open contact, 2=Alarm at closed contact, 3=Contactor | 0 | 3 |  | 0
82 | AYC Heated water periodic operation interval |  | 0 | 168 | h | 24
83 | AYC Heated water periodic operation time |  | 0 | 60 | min | 3
84 | AYC Heated water night temp compensation time 1 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
85 | AYC Heated water night temp compensation start time 1 (hour) |  | 0 | 23 | h | 0
86 | AYC Heated water night temp compensation start time 1 (minutes) |  | 0 | 59 | min | 0
87 | AYC Heated water night temp compensation stop time 1 (hour) |  | 0 | 23 | h | 0
88 | AYC Heated water night temp compensation stop time 1 (minutes) |  | 0 | 59 | min | 0
89 | AYC Heated water night temp compensation time 2 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
90 | AYC Heated water night temp compensation start time 2 (hour) |  | 0 | 23 | h | 0
91 | AYC Heated water night temp compensation start time 2 (minutes) |  | 0 | 59 | min | 0
92 | AYC Heated water night temp compensation stop time 2 (hour) |  | 0 | 23 | h | 0
93 | AYC Heated water night temp compensation stop time 2 (minutes) |  | 0 | 59 | min | 0
94 | AYC Heated water I-time |  | 1 | 600 | s | 60
95 | AYC Chilled water alarm function for pump | 0=Inactive, 1= Alarm at open contact, 2=Alarm at closed contact, 3=Contactor | 0 | 3 |  | 0
96 | AYC Chilled water periodic operation interval |  | 0 | 168 | h | 24
97 | AYC Chilled water periodic operation time |  | 0 | 60 | min | 3
98 | AYC Chilled water night temp compensation time 1 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
99 | AYC Chilled water night temp compensation start time 1 (hour) |  | 0 | 23 | h | 0
100 | AYC Chilled water night temp compensation start time 1 (minutes) |  | 0 | 59 | min | 0
101 | AYC Chilled water night temp compensation stop time 1 (hour) |  | 0 | 23 | h | 0
102 | AYC Chilled water night temp compensation stop time 1 (minutes) |  | 0 | 59 | min | 0
103 | AYC Chilled water night temp compensation time 2 (days) | 0=Inactive, 1=Monday, 2=Tuesday, 3=Wednesday, 4=Thursday, 5=Friday, 6=Saturday, 7=Sunday, 8=Monday to Friday, 9= Monday to Sunday, 10=Saturday to Sunday. | 0 | 10 |  | 0
104 | AYC Chilled water night temp compensation start time 2 (hour) |  | 0 | 23 | h | 0
105 | AYC Chilled water night temp compensation start time 2 (minutes) |  | 0 | 59 | min | 0
106 | AYC Chilledwater night temp compensation stop time 2 (hour) |  | 0 | 23 | h | 0
107 | AYC Chilled water night temp compensation stop time 2 (minutes) |  | 0 | 59 | min | 0
108 | AYC Chilled water I-time |  | 1 | 600 | s | 60
Operation level settings
109 | Communication operation level | 0=auto, 1=total stop, 2=low speed, 3=high speed, 4=normal stop, 5=extended normal stop. | 0 | 5 |  | 0
Time schedule
110 | Year | Setting for the unit's internal clock | 2000 | 2099 |  | 2000
111 | Month | Setting for the unit's internal clock | 1 | 12 |  | 1
112 | Date | Setting for the unit's internal clock | 1 | 31 |  | 1
113 | Hour | Setting for the unit's internal clock | 0 | 23 |  | 0
114 | Minute | Setting for the unit's internal clock | 0 | 59 |  | 0
115 | Second | Setting for the unit's internal clock | 0 | 59 |  | 0
116 | Default action | 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop | 1 | 5 |  | 2
AHU Air flow/duct pressure
117 | Component name | 25=IQlogic | 0 | 999
118 | Application id/AHU Type | 10=GOLD RX, 11=GOLD PX, 12=GOLD CX, 13=GOLD SD/SA,14=GOLD SD/EA, 15=GOLD SD/SA+CX, 16=GOLD SD/SA+EA, 17=GOLD SD/SA+EA+CX | 0 | 999
Fans
119 | SA Fan operation time | Total operation time of the supply air fan presented in days (24h). | 0..9999 | 9999 | days
120 | EA Fan operation time | Total operation time of the extract air fan presented in days (24h). | 0..9999 | 9999 | days
121
122
AHU heat exchange
123 | RHX operation time | Total operation time of the rotary heat exchanger presented in days (24h). | 0 | 9999 | Days
124 | PHX/CHX operation time | Total operation time of the coil heat exchanger presented in days (24h). | 0 | 9999 | Days
AHU Coils
125 | Extra regulation sequence 1 coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
126 | Extra regulation sequence 1 heat operation time | Total operation time of extra regulation heat presented in days (24h). | 0 | 9999 | Days
127 | Extra regulation sequence 1 cool operation time | Total operation time of extra regulation cool presented in days (24h). | 0 | 9999 | Days
128 | Re-heat coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
129 | Re-heat operation time | Total operation time of re-heat presented in days (24h). | 0 | 9999 | Days
130 | Cool coil type | 0=None,1..8=N/A, 9..10=Water, 11..15=N/A | 0 | 15
131 | Cool operation time | Total operation time of cool presented in days (24h). | 0 | 9999 | Days
Xzone coils
132 | Xzone heat, coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
133 | Xzone heat, operation time | Total operation time of Xzone heat presented in days (24h). | 0 | 9999
134 | Xzone cool, coil type | 9..10=Water | 0 | 15
135 | Xzone cool, operation time | Total operation time of Xzone cool presented in days (24h). | 0 | 9999
Pre-heat
136 | Pre-heat coil type | 0=None,1..8=Electric, 9..10=Water, 11..15=Electric | 0 | 15
137 | Pre-heat operation time | Total operation time of pre-heat presented in days (24h). | 0 | 9999 | Days
COOL DX
138 | COOL DX, unit power size |  | 0 | 15
AYC
139 | AYC Heat, operation time | Total operation time of AYC heat presented in days (24h). | 0 | 9999
140 | AYC Cool, operation time | Total operation time of AYC cool presented in days (24h). | 0 | 9999
Operation level
141 | Operation level | 0=Fan not available 1=Alarm stop 2=Manual total stop (on hand terminal) 3=External total stop (digital input) 4=Communication total stop 5=Communication normal stop 6=Communication extended normal stop 7=Time channel total stop 8=Time channel normal stop 9=Time channel extended normal stop 10=Low speed=normal stop 11=SA Fan starting up 12=Fan regulation blocked 13=ReCO2 100% recirculation(1.11) 14=Morning boost stop(1.11) 15=Intermittent night heat stop(1.11) 16=After cooling electric heater 17=COOL DX switch off delay 18=Damper switch off delay 19=Manual low speed (on hand terminal) 20=External low speed (digital input) 21=Extended external low speed 22=Communication low speed 23=Time channel low speed 24=Morning boost low speed 25=Intermittent night heat low speed 26=Manual high speed (on hand terminal) 27=External high speed (digital input) 28=Extended external high speed 29=Communication high speed 30=Time channel high speed 31=Summer night cooling high speed 32=Filter calibration 33=RHX Defrost calibration 34=ReCO2 calibration 35=AHU start up 36=Re-heat ramp down 37=HX ramp down 38=Air adjustment 39=Fans in operation with active fire alarm 40=PX bypass damper adjustment(1.12) | 0 | 100 |  |  | 1.12
Time schedule
142 | Weekday | The internal clock present weekday | 1 | 7
143 | Current action | 1=Total stop, 2=Low speed, 3=High speed, 4=Normal stop, 5=Extended normal stop | 1 | 5
Alarms
144 | Triggered alarm #1 | ((Alarm group - 1) x 15) + alarm number in group=Triggered alarm number. Zero if no triggered alarm. | 0 | 1500
145 | Triggered alarm #2 |  | 0 | 1500
146 | Triggered alarm #3 |  | 0 | 1500
147 | Triggered alarm #4 |  | 0 | 1500
148 | Triggered alarm #5 |  | 0 | 1500
149 | Triggered alarm #6 |  | 0 | 1500
150 | Triggered alarm #7 |  | 0 | 1500
151 | Triggered alarm #8 |  | 0 | 1500
152 | Triggered alarm #9 |  | 0 | 1500
153 | Triggered alarm #10 |  | 0 | 1500
154 | Triggered alarm group #1 | Zero if no triggered alarm group. | 0 | 100
155 | Triggered alarm group #2 |  | 0 | 100
156 | Triggered alarm group #3 |  | 0 | 100
157 | Triggered alarm group #4 |  | 0 | 100
158 | Triggered alarm group #5 |  | 0 | 100
159 | Triggered alarm group #6 |  | 0 | 100
160 | Triggered alarm group #7 |  | 0 | 100
161 | Triggered alarm group #8 |  | 0 | 100
162 | Triggered alarm group #9 |  | 0 | 100
163 | Triggered alarm group #10 |  | 0 | 100
AHU Heat exchange
164 | Cool exchange temperature regulation I-time |  | 1 | 1800 | s | 50 | 1.11
MISC
165 | Dehumidifying function | 0=Inactive, 1=SA, 2=EA | 0 | 2 |  | 0 | 1.12
166 | VOC sensor function | 0=Inactive, 1=Monitoring only, 2=Monitoring and regulation | 0 | 2 |  | 0 | 1.23