## SmokeShield
Smoke/Shield damper reckoner (May be used for A60)
| Damper Area (Square or Rectangular) |  |  | Damper Area - Circular |  |  |  | Velocity/Air flow m/sec |  | TRUE
TRUE
TRUE
| Width in mm |  |  | Diameter in mm |  |  |  | Air volume m3/s
Height in mm
| Area of damper in Sq m = |  | 0 | Area of damper in Sq m = |  |  | 0 | Velocity m/sec - Damper area | 0
[7 empty] | Velocity m/sec - Damper free area |  | 0
| Free Area of damper in Sq m = |  | 0 |  | Maximum permissable Velocity (m/sec) through damper |  |  |  | 15
| Velocity through blades m3/s = |  |  | (Note: - For Circular Width & Height must be cleared)
[5 empty] | Air volume (cubic metres/sec) @ maximum permissable velocity |  |  |  | 0
Convert l/s to m3/s
Input l/s
| Air volume m3/s | 0
Convert m3/hr to m3/s
| Input m3/hr |  |  |  | Pressure drop for above damper size - Enter velocity through damper
| Air volume m3/s | 0
[7 empty] | System velocity (m/sec) through damper |  | 5.5
Convert m3/h to l/s
| Input m3/hr |  |  |  |  | Air volume (cubic metres/sec) @ system velocity |  |  | 0
| Air volume l/s | 0
[5 empty] | Pressure Drop Pa @ System velocity 501 Series dampers |  |  |  | 9.9162
[5 empty] | Pressure Drop Pa @ System velocity 601 Series dampers |  |  |  | 8.0746
Enter dimensions, volumes and velocities into yellow boxes | [8 empty] | Rev date 16/11/15

## Press Drop 501
velocity m/s | pressure drop (pa)
1.9 | 1
2 | 1.2
3 | 2.7
4 | 4.9
5 | 7.8
6 | 12
7 | 17
8 | 21
9 | 27
10 | 33
11
12
13
14
15 | 63
Vel | 5.5
Press Drop | 9.9162
const a | -0.0173
const b | 0.6273
const c | 1.4241
const d | 1.6512

## Press Drop 601
velocity m/s | pressure drop (pa)
2.2 | 1
3 | 2.15
4 | 4
5 | 6.4
6 | 9.5
7 | 14
8 | 18
9 | 24
10 | 28
11
12
13
14
15 | 57
Vel | 5.5
Press Drop | 8.0746
const a | 0.0002
const b | 0.0216
const c | 0.6436
const d | 1.8906
const e | 2.4147