## Overview
GB.Metasys.100915
METASYS N2 open
GOLD sizes 04-80, program version 1.05 and newer versions
Metasys N2 open |  |  |  | Metasys N2 open Virtual Objects
Metasys nodes contains up to 256 Virtual Objects. These virtual objekts can be either one of seven region types; 1) Analog Input, 2) Binary Input, 3) Analog Output, 4) Binary Output, 5) Internal Float, 6) Internal Integer and 7) Internal Byte. The Metasys N2 Master performs reas and write commands to these Virtual Objects and performs cyclic polling of all the virtual objects as well. |  |  |  | A virtual object contains data of a specific type. These types are called Regions. A Metasys N2 node may contain up to 256 Virtual Objects per region, which in all gives a total of 1792 virtual objects. In smaller systems it might be desirable to limit the number of virtual objects to reduce memory consumption. The regions are defined as followed.
Region | Type | Short | Description
Region 1 | Analog Input | AI | 32 bit, IEEE-standard floats.
Region 2 | Binary Input | BI | 1 bit
Region 3 | Analog Output | AO | 32 bit, IEEE-standard floats.
Region 4 | Binary Output | BO | 1 bit
Region 5 | Internal Float | IF | 32 bit, IEEE-standard floats.
Region 6 | Internal Integer | ADI | Signed 16 bit.
Region 7 | Internal Byte | IB | 8 bit.
The 7 regions of a Metasys Virtual Object. |  |  |  | A Metasys Node can contain up to 1792 Virtual Objects.
Virtual Object
Analog Input
Binary Input
Binary Output
Analog Output Output
Internal Float
Internal Integer
Internal Byte
Virtual Object
1
n
2

## Overview parameters
GB.Metasys.100915
Operation mode 1 |  | ADI,110 |  | Extract air filter pressure level |  | AI,53 |  | EA/Room temperature |  | AI,29
Communication operation mode |  | ADI,95 |  | EA filter pressure level limit |  | AI,54 |  | EA/Room temperature setpoint |  | AO,42
Operation mode 2 |  | ADI,111 | [5 empty] | SA Min temperature setpoint |  | AO,43
Operation output |  | BI,8 | [5 empty] | SA Max temperature setpoint |  | AO,44
Low speed output |  | BI,4 |  |  | EA Duct pressure |  | AI,7
High speed output |  | BI,5 |  |  | EA Low speed pressure setpoint |  | AO,13
Damper output |  | BI,9 |  |  | EA High speed pressure setpoint |  | AO,14 | SA Duct Pressure |  | AI,5
Present tripped alarm |  | ADI,101 | [5 empty] | SA Low speed pressure setpoint |  | AO,9
A-alarm |  | BI,6 | [5 empty] | SA High speed pressure setpoint |  | AO,10
B-alarm |  | BI,7
Alarm reset |  | BO,1
[8 empty] | SA Temperature |  | AI,28
[8 empty] | SA Temperature setpoint |  | AO,41
EA Airflow |  | AI,3 | [5 empty] | ERS 1 Diff |  | AO,33
EA Fan level |  | AI,14
EA Low speed airflow setpoint |  | AO,5
EA High speed airflow setpoint |  | AO,6
Outdoor temperature |  | AI,30
Supply air filter pressure level |  | AI,50
SA filter pressure level limit |  | AI,51
Heat exchange regulator |  | AI,57
| SA Airflow |  | AI,1 |  | Reheat level |  | AI,37 | Cooling level |  | AI,40
| SA Fan level |  | AI,13 |  | Heat output |  | BI,1 | Cool output 1 |  | BI,2
| SA Low speed airflow setpoint |  | AO,1 |  | Anti frost temperature |  | AI,33 | Cool output 2 |  | BI,3
| SA High speed airflow setpoint |  | AO,2

## Analog In
GB.Metasys.100915
Analog Input (AI).32 bit IEEE-standard floats (RO).
N2 Idx | Name | Min/Max | Misc
1 | SA Airflow | 0-8200l/s
Present supply airflow.
2 | SA Airflow regulator | 0-8200l/s
Present supply airflow regulator setpoint.
3 | EA Airflow | 0-8200l/s
Present extract airflow.
4 | EA Airflow regulator | 0-8200l/s
Present extract airflow regulator setpoint.
5 | SA Duct pressure | 0-2000Pa
Present supply air duct pressure.
6 | SA Duct pressure regulator | 0-2000Pa
Present supply air duct pressure regulator setpoint.
7 | EA Duct pressure | 0-2000Pa
Present extract air duct pressure.
8 | EA Duct pressure regulator | 0-2000Pa
Present extract air duct pressure regulator setpoint.
9 | SA VAV demand/boost input | 0-100.00%
Present input signal for supply air VAV demand or boosting function.
10 | SA VAV demand regulator | 0-100.00%
Present supply air VAV demand regulator setpoint.
11 | EA VAV demand/boost input | 0-100.00%
Present input signal for extract air VAV demand or boosting function.
12 | EA VAV demand regulator | 0-100.00%
Present supply air VAV demand regulator setpoint.
13 | SA Fan level | 0-100.00%
Present running level for the supply air fan.
14 | EA Fan level | 0-100.00%
Present running level for the extract air fan.
15 | SA Fan effect | 0-6500W
Present power consumption level for the supply air fan.
16 | EA Fan effect | 0-6500W
Present power consumption level for the extract air fan.
17 | SFP | 0.0-9.9
SFP supply air + extract air.
18 | SA Frequency | 0-100.00Hz
Present frequency level for the supply air fan.
19 | EA Frequency | 0-100.00Hz
Present frequency level for the extract air fan.
20 | SA Voltage | 0-500V
Present voltage level for the supply air fan.
21 | EA Voltage | 0-500V
Present voltage level for the extract air fan.
22 | SA Current | 0-30.000A
Present current level for the supply air fan.
23 | EA Current | 0-30.000A
Present current level for the extract air fan.
24 | SA Airflow pressure | 0-2000Pa
Present airflow pressure in the supply air fan inlet.
25 | EA Airflow pressure | 0-2000Pa
Present airflow pressure in the extract air fan inlet.
26 | SA Temp regulator | -55.00-125.00°C
Present supply air temperature regulator setpoint.
27 | EA Temp regulator | -55.00-125.00°C
Present extract air temperature regulator setpoint.
28 | SA Temperature | -55.00-125.00°C
Present supply air temperature.
29 | EA/Room temperature | -55.00-125.00°C
Present extract air/room temperature in the unit.
30 | Outdoor temperatur | -55.00-125.00°C
Present outdoor air temperature in the unit.
31 | EA/Room temperature (external) | -55.00-125.00°C
Present room temperature external from the unit.
32 | Outdoor temperatur (external) | -55.00-125.00°C
Present outdoor air temperature external from the unit.
33 | Anti frost temperature | -55.00-125.00°C
Present anti frost temperature for water reheating coils.
34 | Temperature sensor 3 | -55.00-125.00°C
Present temperature for temp sensor no.3
35 | Temperature sensor 4 | -55.00-125.00°C
Present temperature for temp sensor no.4
36 | Rotary heat exchanger level | 0-100.00%
Present operation level from rotary heat exchanger.
37 | Reheat level | 0-100.00%
Present level of reheat.
38 | SA Down regulation level | 0-100.00%
Present level of supply airflow down regulation.
39 | Extre regulation sequence level | 0-100.00%
Present level of the extra regulation sequence.
40 | Cooling level | 0-100.00%
Present level of cooling.
41 | Heating boost level | 0-100.00%
Present level of heating boost.
42 | Cooling boost level | 0-100.00%
Present level of cooling boost.
43 | HX pressure level | 0-2000Pa
Present pressure drop for the rotary heat exchanger.
44 | HX pressure alarm limit | 0-2000Pa
Present pressure drop alarm limit for the rotary heat exchanger.
45 | HX temperature | 0-100.00°C
Present temperature inside the control unit for the rotary heat exchanger.
46 | Effect reduction level | 0-100.00%
Present level of max output signal for electrical reheaters, active during low supply airflow.
47 | Anti frost temp setpoint/operation | 10.00-16.00°C
Present anti frost temperature setpoint for water reheating coils during unit operation.
48 | Anti frost temp setpoint/stop | 15.00-40.00°C
Present anti frost temperature setpoint for water reheating coils when the unit is in stop.
49 | Anti frost temp alarm limit | 5.00-30.00°C
Setting of antifrost temperature alarm limit.
50 | Supply air filter pressure level | 0-2000Pa
Present supply air filter pressure drop.
51 | Supply air filter pressure alarm limit. | 0-2000Pa
Present supply air filter pressure alarm limit.
52 | Supply air filter pressure level, new | 0-2000Pa
Supply air filter pressure saved from calibration.
53 | Extract air filter pressure level | 0-2000Pa
Present extract air filter pressure drop.
54 | Extract air filter pressure alarm limit. | 0-2000Pa
Present extract air filter pressure alarm limit.
55 | Extract air filter pressure level, new | 0-2000Pa
Extract air filter pressure saved from calibration.
56 | Temperature displacement | -5.00 - 5.00°C
Present temperature displacement from input signal.
57 | Heat exchange regulator | 0-100.00%
Present level of heat exchange regulator RX/CX/PX.
58 | Extract air-humidity | 0-100.00%
Present level of extract air-humidity.
59 | Extract air-humidity temperature | -55.00-125.00°C
Present temperature inside extract air-humidity sensor.
60 | Extract air-dewpoint | -55.00-125.00°C
Calculated extract air-dewpoint.
61 | AYC chilled water temperature | -55.00-125.00°C
Present AYC chilled water temperature.
62 | AYC chilled water temperature regulator | -55.00-125.00°C
Present AYC chilled water temperature regulator setpoint.
63 | AYC chilled water output | 0-100.00%
Present level of AYC chilled water valve output.
64 | Supply air-dewpoint regulator | -55.00-125.00°C
Present supply air-dewpoint regulator setpoint.
65 | Supply air-humidity | 0-100.00%
Present level of supply air-humidity
66 | Supply air-humidity temperature | -55.00-125.00°C
Present temperature inside supply air-humidity sensor.
67 | Supply air-dewpoint | -55.00-125.00°C
Calculated supply air-dewpoint.
68 | C.HX. Temperature | -55.00-125.00°C | PV 2.00
Present temperature of coil heat exchanger.
69 | P.HX. Temperature 1 | -55.00-125.00°C | PV 2.00
Present temperature 1 of plate heat exchanger.
70 | P.HX. Temperature 2 | -55.00-125.00°C | PV 2.00
Present temperature 2 of plate heat exchanger.
71 | P/C.HX. Humidity | 0-100.00% | PV 2.00
Present level of air-humidity in plate/coil heat exchanger.
72 | R.HX. Efficiency | 0-100.00% | PV 2.00
Calculated level of rotary heat exchanger efficiency.
73 | C.HX. Valve output | 0-100.00% | PV 5.00
Present level of coil heat exchanger valve output.
74 | P.HX bypass output | 0-100% | PV 5.00
Present level of plate heat exchanger bypass output.
75 | Supply air prefilter pressure level | 50-300Pa | PV 5.00
Present supply air prefilter pressure drop.
76 | Supply air prefilter pressure alarm limit. | 50-300Pa | PV 5.00
Present supply air prefilter pressure alarm limit.
77 | Supply air prefilter pressure level, new | 50-300Pa | PV 5.00
Supply air prefilter pressure saved from calibration.
78 | Extract air prefilter pressure level | 50-300Pa | PV 5.00
Present extract air prefilter pressure drop.
79 | Extract air prefilter pressure alarm limit. | 50-300Pa | PV 5.00
Present extract air prefilter pressure alarm limit.
80 | Extract air prefilter pressure level, new | 50-300Pa | PV 5.00
Extract air prefilter pressure saved from calibration.
81 | Xzone reheat level | 0-100.00% | PV 5.00
Present level of Xzone reheat.
82 | Xzone anti frost temperature | 0-40.00°C | PV 5.00
Present Xzone anti frost temperature for water reheating coils.
83 | Xzone cooling level | 0-100.00% | PV 5.00
Present level of Xzone cooling.
84 | Xzone SA Temp regulator | 5.00-40.00°C | PV 5.00
Present Xzone supply air temperature regulator setpoint.
85 | Xzone EA Temp regulator | 5.00-40.00°C | PV 5.00
Present Xzone extract air temperature regulator setpoint.
86 | Xzone SA Temperature | 5.00-40.00°C | PV 5.00
Present Xzone supply air temperature.
87 | Xzone EA/Room temperature | 5.00-40.00°C | PV 5.00
Present Xzone extract air/room temperature.
88 | Pre-heating air temperature | 5.00-40.00°C | PV 5.00
Present pre-heating air temperature.
89 | Pre-heating level | 0-100.00% | PV 5.00
Present level of pre-heating.
90 | Pre-heating anti frost temperature | 0-40.00°C | PV 5.00
Present anti frost temperature for water pre-heating coils.
91 | ReCO2 CO2 input | 0-100.00% | PV 5.00
Present input signal for ReCO2 CO2.
92 | ReCO2 internal damper output | 0-100.00% | PV 5.00
Present output signal for ReCO2 internal damper.
93 | ReCO2 external damper output | 0-100.00% | PV 5.00
Present output signal for ReCO2 external damper.
94 | ReCO2 outdoor airflow | 0-8200l/s | PV 5.00
Present ReCO2 outdoor airflow.
95 | ReCO2 outdoor airflow regulator | 0-8200l/s | PV 5.00
Present ReCO2 outdoor airflow regulator setpoint.
96 | ReCO2 outdoor airflow pressure | 0-2000Pa | PV 5.00
Present ReCO2 outdoor airflow pressure.
97 | Supply air-D temperature | -55.00-125.00°C | PV 5.07
Present supply air-D temperature.
98 | Extract air-D temperature | -55.00-125.00°C | PV 5.07
Present extract air-D temperature.
99 | AYC heat temperature | -55.00-125.00°C | PV 5.07
Present AYC heat temperature.
100 | AYC heat temp regulator | -55.00-125.00°C | PV 5.07
Present AYC heat temperature regulator setpoint.
101 | AYC heat valve output | 0-100.00% | PV 5.07
Present level of AYC heat valve output.
102 | Min/Max/Average Sens1Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 1 temperature.
103 | Min/Max/Average Sens2Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 2 temperature.
104 | Min/Max/Average Sens3Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 3 temperature.
105 | Min/Max/Average Sens4Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 4 temperature.

## Int Integer
GB.Metasys.100915
Internal Integer (ADI).Signed 16bit.
N2 Idx | Name | Min/Max | R/W | Misc
1 | SA Fan regulation mode | 0 - 3 | R/W
Setting of regulation type for the supply air fan . 0=Airflow reg, 1=Pressure reg, 2=Demand reg, 3=Slave controlled by EA fan.
2 | EA Fan regulation mode | 0 - 3 | R/W
Setting of regulation type for the extract air fan . 0=Airflow reg, 1=Pressure reg, 2=Demand reg, 3=Slave controlled by SA fan.
3 | ERS Step | 1 - 4 | R/W
Setting of curve when temperature is above breakpoint.
4 | Temperature regulation mode. | 0 - 3 | R/W
Setting of temperature regulation type. 0=ERS 1 reg, 1=ERS 2 reg, 2=SA reg, 3=EA/Room reg.
5 | Cooling off periode | 60 - 900s | R/W
Time setting for cooling off electrical heating coil.
6 | Coil type | 0-20 | R
Present connected reheat coil type.
7 | Cool step time | 0 - 600s | R/W
Time setting between cool step shift.
8 | Cool step time | 0-600s | R
Present time between cool step shift.
9 | Cool restart time | 60 - 900s | R/W
Setting of time between two starts of the cool relays.
10 | Cool relay 1 restart time | 0-900s | R
Present time between two starts of cool relay 1.
11 | Cool relay 2 restart time | 0-900s | R
Present time between two starts of cool relay 2.
12 | Cool regulation mode | 0 - 6 | R/W | PV 3.00
Setting of cool regulation type 0=Controlled 0-10V 1=Controlled 10-0V 2=On/Off 1-step 3=On/Off 2-steps 4=On/Off 3-steps binary 5=CoolDX economi (PV 2.00) 6=CoolDX comfort (PV 3.00)
13 | Heating boost regulation mode. | 0 - 1 | R/W
Setting for heating boost function. 0=Deactive, 1=Active.
14 | Cooling boost regulation mode. | 0 - 5 | R/W | PV 5.00
Setting of cooling boost regulation type. 0=deactive 1=Comfort 2=Economi 3=Sequence 4=Comfort+economy (PV 5.00). 5=Economy+sequence ( PV 5.00).
15 | Filter calibration mode | 0 - 5 | R/W | PV 5.00
Setting for requiered filtercalibration. 0=Deactiv 1=SA+EA-Filter 2=SA-Filter 3=EA-Filter 4=HX 5=ReCO2 (PV 5.00).
16 | Air adjustment time, minutes | 0 - 1727 | R/W
Setting for amount of minutes to air adjustment function.
17 | Air adjustment time, hours | 0 - 28 | R/W
Setting for amount of hours to air adjustment function.
18 | Handterminal language | 0 - 18 | R/W | PV 5.01
0=Svenska 1=Norsk 2=Dansk 3=Suomi 4=English 5=Français 6=Deutsch 7=Polski 8=Český 9=Italiano 10=Español 11=Português 12=Pycckий 13=Eesti 14=Latviesu 15=Lietiviu 16=Nederlands 17=Magyar (New in PV 5.00) 18=Türkçe (New in PV 5.01)
19 | Summer night cool start, hour | 0-23 | R/W
Setting for start time of summer night cooling function.
20 | Summer night cool start, minute | 0-59 | R/W
Setting for start time of summer night cooling function.
21 | Summer night cool stop, hour | 0-23 | R/W
Setting for stop time of summer night cooling function.
22 | Summer night cool stop, minute | 0-59 | R/W
Setting for stop time of summer night cooling function.
23 | Extra regulation sequence cool mode | 0 - 2 | R/W
Setting of extra regulation sequence cool type. 0=Deactive, 1=Comfort, 2=Economi.
24 | Extra regulation sequence heat mode | 0 - 2 | R/W
Setting of extra regulation sequence heat type. 0=Deactive, 1=Comfort, 2=Economi.
25 | Morning boost time, hours | 0-23 | R/W
Setting of morning boost time before normal operation.
26 | Morning boost time, minutes | 0-59 | R/W
Setting of morning boost time before normal operation.
27 | Startup time | 0 - 600s | R/W
Setting of time for startup when the unit regulator is running with fixed signals.
28 | Start delay SA fan. | 0 - 600s | R/W
Setting of start delay time for the supply air fan.
29 | Start delay EA fan. | 0 - 600s | R/W
Setting of start delay time for the extract air fan after supply air fan has started.
30 | Programversion, HMI | 0-10.00 | R
Present programversion for the handterminal.
31 | Programversion, HMI-slave | 0-10.00 | R
Present programversion for the extra handterminal.
32 | Programversion, main controller. | 0-10.00 | R
Present programversion for the main control unit.
33 | Programversion, SA FC-1. | 0-10.00 | R
Present programversion for the supply air frequency converter no.1.
34 | Programversion, SA FC-2. | 0-10.00 | R
Present programversion for the supply air frequency converter no.2.
35 | Programversion, EA FC-1. | 0-10.00 | R
Present programversion for the extract air frequency converter no.1.
36 | Programversion, EA FC-2. | 0-10.00 | R
Present programversion for the extract air frequency converter no.2.
37 | Programversion, HX control unit | 0-10.00 | R
Present programversion for the rotary heat exchange control unit.
38 | Air flow unit | 0 -2 | R/W
Setting of air flow unit presented in the unit's handterminal and WEB. 0=l/s, 1=m3/s, 2=m3/h.
39 | Reserve |  |  | PV 3.00
40 | Year | 2000-2099 | R/W
Setting for the unit's internal clock.
41 | Month | 1-12 | R/W
Setting for the unit's internal clock.
42 | Date | 0-31 | R/W
Setting for the unit's internal clock.
43 | Weekday | 0 - 6 | R
Present weekday for the unit's internal clock.
44 | Hour | 0-23 | R/W
Setting for the unit's internal clock.
45 | Minute | 0-59 | R/W
Setting for the unit's internal clock.
46 | Second | 0-59 | R/W
Setting for the unit's internal clock.
47 | Time channel 1 status | 0-10,16-26 | R/W
Low speed Högfart 0=Inactive 16=Inactive 1=Monday 17=Monday 2=Tuesday 18=Tuesday 3=Wednesday 19=Wednesday 4=Thursday. 20=Thursday 5=Friday 21=Friday 6=Saturday 22=Saturday 7=Sunday 23=Sunday 8=Monday..Friday 24=Monday..Friday 9=Monday..Sunday 25=Monday..Sunday 10=Saturday..Sunday 26=Saturday..Sunday
48 | Time channel 1 start hour | 0-23 | R/W
49 | Time channel 1 start minute | 0-59 | R/W
50 | Time channel 1 stop hour | 0-23 | R/W
51 | Time channel 1 stop minute | 0-59 | R/W
52 | Time channel 2 status | 0-10,16-26 | R/W
53 | Time channel 2 start hour | 0-23 | R/W
54 | Time channel 2 start minute | 0-59 | R/W
55 | Time channel 2 stop hour | 0-23 | R/W
56 | Time channel 2 stop minute | 0-59 | R/W
57 | Time channel 3 status | 0-10,16-26 | R/W
58 | Time channel 3 start hour | 0-23 | R/W
59 | Time channel 3 start minute | 0-59 | R/W
60 | Time channel 3 stop hour | 0-23 | R/W
61 | Time channel 3 stop minute | 0-59 | R/W
62 | Time channel 4 status | 0-10,16-26 | R/W
63 | Time channel 4 start hour | 0-23 | R/W
64 | Time channel 4 start minute | 0-59 | R/W
65 | Time channel 4 stop hour | 0-23 | R/W
66 | Time channel 4 stop minute | 0-59 | R/W
67 | Time channel 5 status | 0-10,16-26 | R/W
68 | Time channel 5 start hour | 0-23 | R/W
69 | Time channel 5 start minute | 0-59 | R/W
70 | Time channel 5 stop hour | 0-23 | R/W
71 | Time channel 5 stop minute | 0-59 | R/W
72 | Time channel 6 status | 0-10,16-26 | R/W
73 | Time channel 6 start hour | 0-23 | R/W
74 | Time channel 6 start minute | 0-59 | R/W
75 | Time channel 6 stop hour | 0-23 | R/W
76 | Time channel 6 stop minute | 0-59 | R/W
77 | Time channel 7 status | 0-10,16-26 | R/W
78 | Time channel 7 start hour | 0-23 | R/W
79 | Time channel 7 start minute | 0-59 | R/W
80 | Time channel 7 stop hour | 0-23 | R/W
81 | Time channel 7 stop minute | 0-59 | R/W
82 | Time channel 8 status | 0-10,16-26 | R/W
83 | Time channel 8 start hour | 0-23 | R/W
84 | Time channel 8 start minute | 0-59 | R/W
85 | Time channel 8 stop hour | 0-23 | R/W
86 | Time channel 8 stop minute | 0-59 | R/W
87 | Extended low speed op. Hours | 0-23 | R/W
Setting for extended low speed operation.
88 | Extended low speed op. Minutes | 0-59 | R/W
Setting for extended low speed operation.
89 | Extended low speed op. Hours | 0-23 | R
Present time for extended low speed operation.
90 | Extended low speed op. Minutes | 0-59 | R
Present time for extended low speed operation.
91 | Extended high speed op. Hours | 0-23 | R/W
Setting for extended low speed operation.
92 | Extended high speed op. Minutes | 0-59 | R/W
Setting for extended low speed operation.
93 | Extended high speed op. Hours | 0-23 | R
Present time for extended high speed operation.
94 | Extended high speed op. Minutes | 0-59 | R
Present time for extended high speed operation.
95 | Communication operation mode | 0 - 4 | R/W | PV 5.00
Setting of unit operation mode from communication. 0=Auto operation. 1=Communication stop 1. 2=Communication low speed. 3=Communication high speed. 4=Communication stop 2 (New in PV 5.00). Summer night cool, intermittent night heat and morning boost functions works at stop 2.
96 | SA Fan operation time | 0-9999 | R
Present operation time for the supply air fan, measured in minutes and present in days (24h).
97 | EA Fan operation time | 0-9999 | R
Present operation time for the extract air fan, measured in minutes and present in days (24h).
98 | Cool operation time | 0-9999 | R
Present operation time for cooling, measured in minutes and present in days (24h).
99 | Heat exchange operation time | 0-9999 | R
Present operation time for heat exchange, measured in minutes and present in days (24h).
100 | Reheat operation time | 0-9999 | R
Present operation time for reheat, measured in minutes and present in days (24h).
101 | Present tripped alarm | 0-200 | R | PV 5.00
Present tripped alarm number with highest priority.
102 | Active not tripped alarm no.1 | 0-200 | R | PV 5.00
Present active alarm in delay.
103 | Active not tripped alarm no.2 | 0-200 | R | PV 5.00
Present active alarm in delay.
104 | Active not tripped alarm no.3 | 0-200 | R | PV 5.00
Present active alarm in delay.
105 | Service periode alarm. | 0-99 | R/W
Setting for delay time in months before service alarm.
106 | External alarm 1 delay | 1 - 600s | R/W
Setting of delay time for external alarm no 1
107 | External alarm 2 delay | 1 - 600s | R/W
Setting of delay time for external alarm no 2
108 | SA Fan size | 04 - 80 | R
Present supply air fan size.
109 | EA Fan size | 04 - 80 | R
Present extract air fan size.
110 | Operation mode 1 | 0 - 18 | R | PV 5.00
0=Manual stop. 1=Ext. stop. 2=Com. stop 1. 3=Manual high speed. 4=Summer night cooling. 5=Int. night heat. 6=Manual low speed. 7=Ext. high speed. 8=Com. high speed. 9=Year channel stop. 10=Year channel high speed. 11=Year channel low speed. 12=Time channel high speed. 13=Ext. low speed. 14=Com. low speed. 15=Time channel low speed. 16=Time channel stop. 17=Low speed=stop. 18=Com. stop 2. (New in PV 5.00)
111 | Operation mode 2 | 0 - 22 | R | PV 5.00
0= 1=Coold air recovery. 2=Cooling boost. 3=SA down regulation. 4=HX defrosting. 5=Anti frost func. active. 6=Effect reduction. 7=Startup. 8=Zero calibration. 9=Extended low speed. 10=Extended high speed. 11=Air adjustment. 12=Cooling off. 13=Purging R.HX. 14=Extended R.HX. op. 15=Filter calibration. 16=R.HX. calibration 17=Morning boost. 18=Heating boost. 19=Alarm. 20=CoolDX pressure reduction. (PV 2.00) 21=Startup extract air fan (New in 4.00) R.HX speed limited. (Only in PV 2.00-2.02) 22=Fan heat retention (New in PV 5.00)
112 | Operation mode, manual | 0 - 3 | R
Present manual operation set on the unit's handterminal 0=Stop, 1=Auto operation, 2=Manual low speed, 3=Manual high speed.
113 | Copy of Binary Input 1-16 | 0-65535 | R
Bit 0 = Binary Input 1
Bit 1 = Binary Input 2
Bit 15 = Binary Input 16
114 | Copy of Binary Input 17-32 | 0-65535 | R
Bit 0 = Binary Input 17
Bit 1 = Binary Input 18
Bit 15 = Binary Input 32
115 | Copy of Binary Input 33-48 | 0-65535 | R
Bit 0 = Binary Input 33
Bit 1 = Binary Input 34
Bit 15 = Binary Input 48
116 | Copy of Binary Output 1-16 | 0-65535 | R/W
Bit 0 = Binary Output 1
Bit 1 = Binary Output 2
Bit 15 = Binary Output 16
117 | Copy of Binary Output 17-32 | 0-65535 | R/W
Bit 0 = Binary Output 17
Bit 1 = Binary Output 18
Bit 15 = Binary Output 32
118 | Copy of Binary Output 33-48 | 0-65535 | R/W
Bit 0 = Binary Output 33
Bit 1 = Binary Output 34
Bit 15 = Binary Output 48
119 | Heat relay periodic func. | 0-3 | R/W | PV 2.02
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
120 | Cool relay 1 periodic func. | 0-3 | R/W | PV 2.02
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
121 | Cool relay 2 periodic func. | 0-3 | R/W | PV 2.02
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
122 | Cool periodic op. time | 0-60min | R/W | PV 2.02
Setting of periodic op. time (minute).
123 | Cool interval | 0-168h | R/W | PV 2.02
Setting of cool interval time (hour).
124 | EA/Room temperature (external) func. | 0-3 | R/W | PV 5.15
Setting of EA/Room temperature (external) function. 0=Inactive. 1=Input signal on terminal 40..41. 2=Communication (Vpac 5 index 123). 3=Min/Max/Average (PV 5.15).
125 | Outdoor temperature (external) func. | 0-2 | R/W | PV 3.00
Setting of outdoor temperature (external) function. 0=Inactive. 1=Input signal on terminal 38..39. 2=Communication (AO 113).
126 | Timeout temperature com. | 0-9999min | R/W | PV 3.00
Setting of timeout for temperature via communication (AO 112, AO 113).
127 | Flow at fire function. | 0-3 | R/W | PV 3.00
Setting for activating the air fan operation at fire function 0=Inactive. 1=SA. 2=EA. 3=SA+EA.
128 | Air fan down regulation func. | 0-2 | R/W | PV 3.00
Setting for activating the air fan down regulation function 0=Inactive. 1=SA. 2=SA+EA.
129 | Temperature alarm time. | 1-999s | R/W | PV 3.00
Setting of delay time for temperature alarm (no.80).
130 | Year channel 1 function. | 0 - 3 | R/W | PV 3.00
0=Inactive. 1=Stop. 2=Low speed. 3=High speed.
131 | Year channel 1 start year. | 2000 - 2099 | R/W | PV 3.00
132 | Year channel 1 start month. | 1 - 12 | R/W | PV 3.00
133 | Year channel 1 start date. | 1 - 31 | R/W | PV 3.00
134 | Year channel 1 start hour. | 0 - 23 | R/W | PV 3.00
135 | Year channel 1 start minute. | 0 - 59 | R/W | PV 3.00
136 | Year channel 1 stop year. | 2000 - 2099 | R/W | PV 3.00
137 | Year channel 1 stop month. | 1 - 12 | R/W | PV 3.00
138 | Year channel 1 stop date. | 1 - 31 | R/W | PV 3.00
139 | Year channel 1 stop hour. | 0 - 23 | R/W | PV 3.00
140 | Year channel 1 stop minute. | 0 - 59 | R/W | PV 3.00
141 | Year channel 2 function. | 0 - 3 | R/W | PV 3.00
142 | Year channel 2 start year. | 2000 - 2099 | R/W | PV 3.00
143 | Year channel 2 start month. | 1 - 12 | R/W | PV 3.00
144 | Year channel 2 start date. | 1 - 31 | R/W | PV 3.00
145 | Year channel 2 start hour. | 0 - 23 | R/W | PV 3.00
146 | Year channel 2 start minute. | 0 - 59 | R/W | PV 3.00
147 | Year channel 2 stop year. | 2000 - 2099 | R/W | PV 3.00
148 | Year channel 2 stop month. | 1 - 12 | R/W | PV 3.00
149 | Year channel 2 stop date. | 1 - 31 | R/W | PV 3.00
150 | Year channel 2 stop hour. | 0 - 23 | R/W | PV 3.00
151 | Year channel 2 stop minute. | 0 - 59 | R/W | PV 3.00
152 | Year channel 3 function. | 0 - 3 | R/W | PV 3.00
153 | Year channel 3 start year. | 2000 - 2099 | R/W | PV 3.00
154 | Year channel 3 start month. | 1 - 12 | R/W | PV 3.00
155 | Year channel 3 start date. | 1 - 31 | R/W | PV 3.00
156 | Year channel 3 start hour. | 0 - 23 | R/W | PV 3.00
157 | Year channel 3 start minute. | 0 - 59 | R/W | PV 3.00
158 | Year channel 3 stop year. | 2000 - 2099 | R/W | PV 3.00
159 | Year channel 3 stop month. | 1 - 12 | R/W | PV 3.00
160 | Year channel 3 stop date. | 1 - 31 | R/W | PV 3.00
161 | Year channel 3 stop hour. | 0 - 23 | R/W | PV 3.00
162 | Year channel 3 stop minute. | 0 - 59 | R/W | PV 3.00
163 | Year channel 4 function. | 0 - 3 | R/W | PV 3.00
164 | Year channel 4 start year. | 2000 - 2099 | R/W | PV 3.00
165 | Year channel 4 start month. | 1 - 12 | R/W | PV 3.00
166 | Year channel 4 start date. | 1 - 31 | R/W | PV 3.00
167 | Year channel 4 start hour. | 0 - 23 | R/W | PV 3.00
168 | Year channel 4 start minute. | 0 - 59 | R/W | PV 3.00
169 | Year channel 4 stop year. | 2000 - 2099 | R/W | PV 3.00
170 | Year channel 4 stop month. | 1 - 12 | R/W | PV 3.00
171 | Year channel 4 stop date. | 1 - 31 | R/W | PV 3.00
172 | Year channel 4 stop hour. | 0 - 23 | R/W | PV 3.00
173 | Year channel 4 stop minute. | 0 - 59 | R/W | PV 3.00
174 | Year channel 5 function. | 0 - 3 | R/W | PV 3.00
175 | Year channel 5 start year. | 2000 - 2099 | R/W | PV 3.00
176 | Year channel 5 start month. | 1 - 12 | R/W | PV 3.00
177 | Year channel 5 start date. | 1 - 31 | R/W | PV 3.00
178 | Year channel 5 start hour. | 0 - 23 | R/W | PV 3.00
179 | Year channel 5 start minute. | 0 - 59 | R/W | PV 3.00
180 | Year channel 5 stop year. | 2000 - 2099 | R/W | PV 3.00
181 | Year channel 5 stop month. | 1 - 12 | R/W | PV 3.00
182 | Year channel 5 stop date. | 1 - 31 | R/W | PV 3.00
183 | Year channel 5 stop hour. | 0 - 23 | R/W | PV 3.00
184 | Year channel 5 stop minute. | 0 - 59 | R/W | PV 3.00
185 | Year channel 6 function. | 0 - 3 | R/W | PV 3.00
186 | Year channel 6 start year. | 2000 - 2099 | R/W | PV 3.00
187 | Year channel 6 start month. | 1 - 12 | R/W | PV 3.00
188 | Year channel 6 start date. | 1 - 31 | R/W | PV 3.00
189 | Year channel 6 start hour. | 0 - 23 | R/W | PV 3.00
190 | Year channel 6 start minute. | 0 - 59 | R/W | PV 3.00
191 | Year channel 6 stop year. | 2000 - 2099 | R/W | PV 3.00
192 | Year channel 6 stop month. | 1 - 12 | R/W | PV 3.00
193 | Year channel 6 stop date. | 1 - 31 | R/W | PV 3.00
194 | Year channel 6 stop hour. | 0 - 23 | R/W | PV 3.00
195 | Year channel 6 stop minute. | 0 - 59 | R/W | PV 3.00
196 | Year channel 7 function. | 0 - 3 | R/W | PV 3.00
197 | Year channel 7 start year. | 2000 - 2099 | R/W | PV 3.00
198 | Year channel 7 start month. | 1 - 12 | R/W | PV 3.00
199 | Year channel 7 start date. | 1 - 31 | R/W | PV 3.00
200 | Year channel 7 start hour. | 0 - 23 | R/W | PV 3.00
201 | Year channel 7 start minute. | 0 - 59 | R/W | PV 3.00
202 | Year channel 7 stop year. | 2000 - 2099 | R/W | PV 3.00
203 | Year channel 7 stop month. | 1 - 12 | R/W | PV 3.00
204 | Year channel 7 stop date. | 1 - 31 | R/W | PV 3.00
205 | Year channel 7 stop hour. | 0 - 23 | R/W | PV 3.00
206 | Year channel 7 stop minute. | 0 - 59 | R/W | PV 3.00
207 | Year channel 8 function. | 0 - 3 | R/W | PV 3.00
208 | Year channel 8 start year. | 2000 - 2099 | R/W | PV 3.00
209 | Year channel 8 start month. | 1 - 12 | R/W | PV 3.00
210 | Year channel 8 start date. | 1 - 31 | R/W | PV 3.00
211 | Year channel 8 start hour. | 0 - 23 | R/W | PV 3.00
212 | Year channel 8 start minute. | 0 - 59 | R/W | PV 3.00
213 | Year channel 8 stop year. | 2000 - 2099 | R/W | PV 3.00
214 | Year channel 8 stop month. | 1 - 12 | R/W | PV 3.00
215 | Year channel 8 stop date. | 1 - 31 | R/W | PV 3.00
216 | Year channel 8 stop hour. | 0 - 23 | R/W | PV 3.00
217 | Year channel 8 stop minute. | 0 - 59 | R/W | PV 3.00
218 | Filter select. | 0 - 3 | R/W | PV 5.00
Setting for filter select function. 0=Inactive. 1=Supply air. 2=Extract air. 3=SA+EA.
219 | Prefilter select. | 0 - 3 | R/W | PV 5.00
Setting for prefilter select function. 0=Inactive. 1=Supply air. 2=Extract air. 3=SA+EA.
220 | Prefilter calibration mode. | 0 - 3 | R/W | PV 5.00
Setting for requiered filtercalibration. 0=Inactive. 1=SA+EA-Filter. 2=SA-Filter. 3=EA-Filter.
221 | Xzone cool step time | 0-600s | R | PV 5.00
Present time between Xzone cool step shift.
222 | Xzone cool relay 1 restart time | 0-900s | R | PV 5.00
Present time between two starts of Xzone cool relay 1.
223 | Xzone cool relay 2 restart time | 0-900s | R | PV 5.00
Present time between two starts of Xzone cool relay 2.
224 | Xzone reheat function. | 0 - 4 | R/W | PV 5.00
Setting for Xzone reheat function. 0=Inactive. 1=El. coil P/P. 2=El. coil 0-10V. 3=Water coil with FP. 4=Water coil without FP.
225 | Xzone cooling function. | 0 - 5 | R/W | PV 5.00
Setting for Xzone cooling function. 0=Inactive. 1=0-10V. 2=10-0V. 3=On/off 1. 4=On/off 2. 5=On/off 3.
226 | Xzone temperature regulation mode. | 0 - 3 | R/W | PV 5.00
Setting of Xzone temperature regulation type. 0=ERS 1 reg. 1=ERS 2 reg. 2=SA reg. 3=EA/Room reg.
227 | Xzone ERS Step. | 1 - 4 | R/W | PV 5.00
Setting of Xzone curve when temperature is above breakpoint.
228 | Preheating function. | 0 - 4 | R/W | PV 5.00
Setting of preheating function. 0=Inactive. 1=El. coil P/P. 2=El. coil 0-10V. 3=Water coil with FP. 4=Water coil without FP.
229 | ReCO2 CO2 function. | 0 - 2 | R/W | PV 5.00
Setting of ReCO2 CO2 function. 0=Inactive. 1=CO2. 2=CO2+flow.
230 | ReCO2 cooling function. | 0 - 2 | R/W | PV 5.00
Setting of ReCO2 cooling function. 0=Inactive. 1=Comfort. 2=Economy.
231 | ReCO2 heating function. | 0 - 2 | R/W | PV 5.00
Setting of ReCO2 heating function. 0=Inactive. 1=Comfort. 2=Economy.
232 | Preheat operation time | 0-9999 | R | PV 5.00
Present operation time for preheat, measured in minutes and present in days (24h).
233 | Xzone cool operation time | 0-9999 | R | PV 5.00
Present operation time for Xzone cooling, measured in minutes and present in days (24h).
234 | Xzone reheat operation time | 0-9999 | R | PV 5.00
Present operation time for Xzone reheat, measured in minutes and present in days (24h).
235 | AYC function. | 0 - 3 | R/W | PV 5.07
Setting of AYC function. 0=Inactive. 1=Cool. 2=Heat. 3=Cool+heat.
236 | AYC night comp. channel. | 1 - 2 | R/W | PV 5.07
Setting of AYC night compensation channel. 1=Channel 1. 2=Channel 2.
237 | AYC channel start hour. | 0-23h | R/W | PV 5.07
Setting of AYC channel start time (hour).
238 | AYC channel start minute. | 0-59min | R/W | PV 5.07
Setting of AYC channel start time (minute).
239 | AYC channel stop hour. | 0-23h | R/W | PV 5.07
Setting of AYC channel stop time (hour).
240 | AYC channel stop minute. | 0-59min | R/W | PV 5.07
Setting of AYC channel stop time (minute).
241 | AYC channel period. | 0-10 | R/W | PV 5.07
Setting of AYC channel period. 0=Inactive 1=Monday 2=Tuesday 3=Wednesday 4=Thursday 5=Friday 6=Saturday 7=Sunday 8=Monday..Friday 9=Monday..Sunday 10=Saturday..Sunday
242 | AYC heat pump alarm. | 0 - 3 | R/W | PV 5.07
Setting for selecting the AYC heated water pump alarm function. 0=Inactive. 1=Open. 2=Closed. 3=Contactor.
243 | AYC heat per op function. | 0 - 3 | R/W | PV 5.07
Setting for selecting the AYC heated water periodic operation function. 0=Inactive. 1=Pump. 2=Pump+valve. 3=Valve.
244 | AYC heat per op time. | 0-60min | R/W | PV 5.07
AYC periodic operation of heated water, time (minute) setting.
245 | AYC heat per op interval. | 0-168h | R/W | PV 5.07
AYC periodic operation of heated water, interval time (hour) setting.
246 | AYC cool pump alarm. | 0 - 3 | R/W | PV 5.07
Setting for selecting the AYC chilled water pump alarm function. 0=Inactive. 1=Open. 2=Closed. 3=Contactor.
247 | AYC cool per op function. | 0 - 3 | R/W | PV 5.07
Setting for selecting the AYC chilled water periodic operation function. 0=Inactive. 1=Pump. 2=Pump+valve. 3=Valve.
248 | AYC cool per op time. | 0-60min | R/W | PV 5.07
AYC periodic operation of chilled water, time (minute) setting.
249 | AYC cool per op interval. | 0-168h | R/W | PV 5.07
AYC periodic operation of chilled water, interval time (hour) setting.
250 | IO-mod 3 output 1 function. | 0 - 10 | R/W | PV 5.07
Setting of I/O-module no. 3 relay 1 output. 0=Cooling boost. 1=Heating boost. 2=Cooling. 3=Heat exchange. 4=Reheat. 5=Down regulation. 6=Effect reduction. 7=Intermittent night heat. 8=Summer night cooling. 9=Morning boost. 10=Heat exchange defrost.
251 | IO-mod 3 output 2 function. | 0 - 10 | R/W | PV 5.07
Setting of I/O-module no. 3 relay 2 output. 0=Cooling boost. 1=Heating boost. 2=Cooling. 3=Heat exchange. 4=Reheat. 5=Down regulation. 6=Effect reduction. 7=Intermittent night heat. 8=Summer night cooling. 9=Morning boost. 10=Heat exchange defrost.
252 | Humid reg. func. | 0 - 2 | R/W | PV 5.10
Setting for selecting humidifying function. 0=Inactive. 1=Supply air. 2=Extract air.
253 | Min/Max/Average SensNumber | 1 - 4 | R/W | PV 5.15
Setting for selecting numbers of sensors to the Min/Max/Average function.
254 | Min/Max/Average SensFunction | 0 - 2 | R/W | PV 5.15
Setting for selecting sensor function. 0=Min. 1=Max. 2=Average.

## Binary In
GB.Metasys.100915
Binary Input (BI).1bit (RO).
N2 Idx | Name | Min/Max | Misc
1 | Heat output | 0-1
Status for relay output.
2 | Cool output 1 | 0-1
Status for relay output.
3 | Cool output 2 | 0-1
Status for relay output.
4 | Low speed output | 0-1
Status for relay output.
5 | High speed output | 0-1
Status for relay output.
6 | A-alarm. | 0-1
Status for relay output.
7 | B-alarm. | 0-1
Status for relay output.
8 | Operation output | 0-1
Status for relay output.
9 | Damper output | 0-1
Status for relay output.
10 | External low speed input | 0-1
Status for digital input.
11 | External high speed input | 0-1
Status for digital input.
12 | External alarm 1 input | 0-1
Status for digital input.
13 | External alarm 2 input | 0-1
Status for digital input.
14 | External fire alarm input. | 0-1
Status for digital input.
15 | External stop input | 0-1
Status for digital input.
16 | DIP Switch 1 | 0-1
Status for dip switch setting.
17 | DIP Switch 2 | 0-1
Status for dip switch setting.
18 | DIP Switch 3 | 0-1
Status for dip switch setting.
19 | DIP Switch 4 | 0-1
Status for dip switch setting.
20 | DIP Switch 5 | 0-1
Status for dip switch setting.
21 | DIP Switch 6 | 0-1
Status for dip switch setting.
22 | AYC heat pump output | 0-1 | PV 5.07
Status for AYC heat pump output.
23 | AYC cool pump output | 0-1 | PV 5.07
Status for AYC cool pump output.
24 | C.HX. pump output | 0-1 | PV 2.00
Status for coil heat exchanger pump output.
25 | R.HX rotation monitor | 0-1 | PV 3.00
Status from the rotation detector.
26 | Xzone heat output | 0-1 | PV 5.00
Status for relay output.
27 | Xzone cool output 1 | 0-1 | PV 5.00
Status for relay output.
28 | Xzone cool output 2 | 0-1 | PV 5.00
Status for relay output.
29 | Pre-heat output | 0-1 | PV 5.00
Status for relay output.
30 | IO-mod 3 output 1 | 0-1 | PV 5.07
Status for I/O-module no. 3 relay 1 output.
31 | IO-mod 3 output 2 | 0-1 | PV 5.07
Status for I/O-module no. 3 relay 2 output.
32 | IO-mod 4 output 1 | 0-1 | PV 5.10
Status for I/O-module no. 4 relay 1 output.
33 | Reserve 12
34 | Reserve 13
35 | Reserve 14
36 | Reserve 15
37 | Reserve 16
38 | Reserve 17
39 | Reserve 18
40 | Reserve 19
41 | Reserve 20
42 | Reserve 21
43 | Reserve 22
44 | Reserve 23
45 | Reserve 24
46 | Reserve 25
47 | Reserve 26
48 | Reserve 27
49 | Alarm number 1 | 0-1
Status if alarm number 1 is active.
50 | Alarm number 2 | 0-1
Status if alarm number 2 is active.
51 | Alarm number 3 | 0-1
Status if alarm number 3 is active.
228 | Alarm number 180 | 0-1 | PV 5.00
Status if alarm number 100 is active.
229 | Info number 1 | 0-1 | PV 5.00
Status if info number 1 is active.
230 | Info number 2 | 0-1 | PV 5.00
Status if info number 2 is active.
231 | Info number 3 | 0-1 | PV 5.00
Status if info number 3 is active.
248 | Info number 20 | 0-1 | PV 5.00
Status if info number 100 is active.

## Analog Out
GB.Metasys.100915
Analog Output (AO).32bit IEEE-standard floats (R/W).
N2 Idx | Name | Min/Max | Misc
1 | SA Low speed airflow setpoint | 0-8200l/s
Supply airflow setpoint for the unit when running in low speed operation.
2 | SA High speed airflow setpoint | 0-8200l/s
Supply airflow setpoint for the unit when running in high speed operation.
3 | SA Max speed airflow setpoint | 0-8200l/s
Supply airflow max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
4 | SA Min speed airflow setpoint | 0-8200l/s
Supply airflow min. limit for the unit when the low/high speed operation setpoint is altered when running in fan regulation mode VAV demand.
5 | EA Low speed airflow setpoint | 0-8200l/s
Extract airflow setpoint for the unit when running in low speed operation.
6 | EA High speed airflow setpoint | 0-8200l/s
Extract airflow setpoint for the unit when running in high speed operation.
7 | EA Max speed airflow setpoint | 0-8200l/s
Extract airflow max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
8 | EA Min speed airflow setpoint | 0-8200l/s
Extract airflow min. limit for the unit when the low/high speed operation setpoint is altered when running in fan regulation mode VAV demand.
9 | SA Low speed pressure setpoint | 0-750Pa
Supply air duct pressure setpoint for the unit when running in low speed operation.
10 | SA High speed pressure setpoint | 20-750Pa
Supply air duct pressure for the unit when running in high speed operation.
11 | SA Max speed output signal | 10.00-100.00%
Max. limit for the supply air fan speed when running in pressure regulation mode.
12 | SA Max speed pressure setpoint | 20-750Pa
Supply air duct pressure max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
13 | EA Low speed pressure setpoint | 0-750Pa
Extract air duct pressure setpoint for the unit when running in low speed operation.
14 | EA High speed pressure setpoint | 20-750Pa
Extract air duct pressure setpoint for the unit when running in high speed operation.
15 | EA Max speed output signal | 10.00-100.00%
Max. limit for the extract air fan speed when running in pressure regulation mode.
16 | EA Max speed pressure setpoint | 20-750Pa
Extract air duct pressure max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
17 | SA Low speed demand setpoint | 0-100.00%
Supply air setpoint for the 0-10V input signal on terminal 30..31 for the unit when running in low speed operation.
18 | SA High speed demand setpoint | 0-100.00%
Supply air setpoint for the 0-10V input signal on terminal 30..31 for the unit when running in high speed operation.
19 | EA Low speed demand setpoint | 0-100.00%
Extract air setpoint for the 0-10V input signal on terminal 32..33 for the unit when running in low speed operation.
20 | EA High speed demand setpoint | 0-100.00%
Extract air setpoint for the 0-10V input signal on terminal 32..33 for the unit when running in high speed operation.
21 | SA Airflow regulation zone | 1.00 - 10.00
Supply airflow regulation zone setting in % of the present airflow setpoint that the regulator is allowed to work within.
22 | SA Airflow C-factor | 0.005 - 2.500
Supply airflow regulator affection setting.
23 | EA Airflow regulation zone | 1.00 - 10.00
Extract airflow regulation zone setting in % of the present airflow setpoint that the regulator is allowed to work within.
24 | EA Airflow C-factor | 0.005 - 2.500
Extract airflow regulator affection setting.
25 | SA Pressure regulation zone | 1.00 - 10.00
Supply air pressure regulation zone setting in % of the present duct pressure setpoint that the regulator is allowed to work within.
26 | SA Pressure C-factor | 0.005 - 2.500
Supply air pressure regulator affection setting.
27 | EA Pressure regulation zone | 1.00 - 10.00
Extract air pressure regulation zone setting in % of the present duct pressure setpoint that the regulator is allowed to work within.
28 | EA Pressure C-factor | 0.005 - 2.500
Extract air pressure regulator affection setting.
29 | SA Demand P-band. | 1.00 - 100.00
Supply air demand regulator P-band setting.
30 | SA Demand C-factor | 0.005 - 2.500
Supply air demand regulator affection setting.
31 | EA Demand P-band. | 1.00 - 100.00
Extract air demand regulator P-band setting.
32 | EA Demand C-factor | 0.005 - 2.500
Extract air demand regulator affection setting.
33 | ERS 1 Diff | 1.00 - 7.00°C
Supply air temperature difference setting accordning to the diagram for ERS 1.
34 | ERS 1 Breakpoint | 12.00 - 26.00°C
Breakpoint setting accordning to the diagram for ERS 1.
35 | ERS 2 Breakpoint X1 | 10.00-38.00°C
Breakpoint X1 setting accordning to the diagram for ERS 2.
36 | ERS 2 Breakpoint Y1 | 10.00-40.00°C
Breakpoint Y1 setting accordning to the diagram for ERS 2.
37 | ERS 2 Breakpoint X2 | 11.00-39.00°C
Breakpoint X2 setting accordning to the diagram for ERS 2.
38 | ERS 2 Breakpoint Y2 | 10.00-40.00°C
Breakpoint Y2 setting accordning to the diagram for ERS 2.
39 | ERS 2 Breakpoint X3 | 12.00-40.00°C
Breakpoint X3 setting accordning to the diagram for ERS 2.
40 | ERS 2 Breakpoint Y3 | 10.00-40.00°C
Breakpoint Y3 setting accordning to the diagram for ERS 2.
41 | SA Temperature setpoint | 10.00-40.00°C
Supply air temperature setting, for supply air temp regulation mode.
42 | EA/Room Temperature setpoint | 10.00-40.00°C
Extract air/room temperature setting, for Extract air/room temp regulation mode.
43 | SA Min temp setpoint | 8.00-20.00°C
Supply air min.setpoint during EA/room regulation mode.
44 | SA Max temp setpoint | 16.00-50.00°C
Supply air max.setpoint during EA/room regulation mode.
45 | SA Temperature P-band | 1.00 - 40.00 | PV 5.00
Supply air temperature regulator P-band setting.
46 | EA/Room Temperature P-band | 1.00 - 40.00 | PV 5.00
Extract air/room temperature regulator P-band setting.
47 | SA HX. Reg C-factor | 0.000 - 2.500
Supply air heat exchange regulator affection setting.
48 | EA/Room HX. Reg C-factor | 0.000 - 2.500
Extract air/room heat exchange regulator affection setting.
49 | SA Heat Reg C-factor | 0.000 - 2.500
Supply air reheat regulator affection setting.
50 | EA/Room Heat Reg C-factor | 0.000 - 2.500
Extract air/room reheat regulator affection setting.
51 | SA Extra Reg heat C-factor | 0.000 - 2.500
Supply air extra regulation sequence for reheating regulator affection setting.
52 | SA Extra Reg cool C-factor | 0.000 - 2.500
Supply air extra regulation sequence for cooling regulator affection setting.
53 | EA Extra Reg heat C-factor | 0.000 - 2.500
Extract air extra regulation sequence for reheating regulator affection setting.
54 | EA Extra Reg cool C-factor | 0.000 - 2.500
Extract air extra regulation sequence for cooling regulator affection setting.
55 | SA Down regulation Reg C-factor | 0.000 - 2.500
Supply air reheat regulator affection setting.
56 | Reserve
57 | SA Cool reg C-factor | 0.000 - 2.500
Supply air cool regulator affection setting.
58 | EA/Room Cool reg C-factor | 0.000 - 2.500
Extract air/room cool regulator affection setting.
59 | SA Cooling boost C-factor | 0.000 - 2.500
Supply air cooling boost affection setting.
60 | EA/Room Cooling boost reg C-factor | 0.000 - 2.500
Extract air/room cooling boost regulator affection setting.
61 | HX Pressure alarm set. | 30 - 100Pa
Heat exchange pressure alarm limit setting (alarm no.38).
62 | P/C.HX. defrost P-band | 1.00 - 40.00 | PV 2.00
Plate/coil heat exchange defrost P-band setting.
63 | P/C.HX. defrost C-factor | 0.000 - 2.500 | PV 2.00
Plate/coil heat exchange defrost C-factor setting.
64 | Cooling off set. | 10 - 50%
Cooling off airflow setting in % of max. airflow.
65 | SA Down regulation neautral zone | 0.00-10.00°C
Neutral zone setting before downregulation is permitted.
66 | Cool Outdoor temp limit.1 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 1.
67 | Cool Outdoor temp limit.2 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 2.
68 | Cool Outdoor temp limit.3 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 3.
69 | Temperature reg. Neutral zone | 0.50-10.00°C
Neutral zone setting before shift between heating and cooling.
70 | SA Cool min air flow | 0-8200l/s
Supply air min. air flow setting for cooling.
71 | EA Cool min air flow | 0-8200l/s
Extract air min. air flow setting for cooling.
72 | Heating boost start limit | 0.00-40.00°C
Heating boost start temperature limit.
73 | Cooling boost start limit | 0.00-40.00°C
Cooling boost (comfort) start temperature limit.
74 | SA Filter alarm limit | 50-300Pa
Supply air filter pressure alarm limit setting.
75 | EA Filter alarm limit | 50-300Pa
Extract air filter pressure alarm limit setting.
76 | Int. Night heat room start temp | 5.00-25.00°C
Intermittent night heat function, extract air temperature setting for start.
77 | Int. Night heat room stop temp | 5.00-25.00°C
Intermittent night heat function, extract air temperature setting for stop.
78 | Int. Night heat SA temp setpoint | 5.00-40.00°C
Intermittent night heat function, supply air temperature setpoint during night heat.
79 | Int. Night heat SA airflow setpoint | 0-8200l/s
Intermittent night heat function, supply airflow setpoint during night heat.
80 | Int. Night heat EA airflow setpoint | 0-8200l/s
Intermittent night heat function, extract airflow setpoint during night heat.
81 | Summer night cool EA start temp | 17.00-27.00°C
Summer night cool function, extract air temperature setting for start.
82 | Summer night cool EA stop temp | 12.00-22.00°C
Summer night cool function, extract air temperature setting for stop.
83 | Summer night cool outdoor temp limit | 5.00-15.00°C
Summer night cool function, outdoor temperature limit.
84 | Summer night cool SA temp setpoint | 10.00-20.00°C
Summer night cool function, supply air temperature setpoint during summer night cool.
85 | Outdoor temp comp. Winter X1. | -30.00-(-10.00)°C
Endpoint of winter compensation.
86 | Outdoor temp comp. Winter X2. | -10.00-15.00°C
Startpoint of winter compensation.
87 | Outdoor temp comp. Winter Y1. | 0.00-10.00°C
Level of winter compensation at X1.
88 | Outdoor temp comp. Summer X3. | 15.00-25.00°C
Startpoint of summer compensation.
89 | Outdoor temp comp. Summer X4. | 25.00-40.00°C
Endpoint of summer compensation.
90 | Outdoor temp comp. Summer Y2. | -10.00-10.00°C
Level of summer compensation at X4.
91 | Outdoor airflow comp. Winter X1. | -30.00-(-10.00)°C
Endpoint of winter compensation.
92 | Outdoor airflow comp. Winter X2. | -10.00-15.00°C
Startpoint of winter compensation.
93 | Outdoor airflow comp. Winter Y1. | 0-50.00%
Level of airflow compensation at X1.
94 | Extra Reg. Sequence max output | 0-100.00%
Maximum output signal setting for the extra regulation sequence.
95 | EA/Room min temp alarm limit | 8.00-20.00°C
Setting for min extract air /room temp alarm no.40.
96 | SA Deviation alarm limit | 2.00-15.00°C
Setting for supply air temperature below present setpoint, alarm no.41.
97 | Reserve
98 | Int. Night heat SA pressure setpoint | 20-750Pa
Intermittent night heat function, supply pressure setpoint during night heat.
99 | Int. Night heat EA pressure setpoint | 20-750Pa
Intermittent night heat function, extract pressure setpoint during night heat.
100 | Slave control C-factor | 0.5 - 2.0 | PV 5.07
Slave regulator affection setting.
101 | SA dehumid P-band | 1.00 - 40.00 | PV 5.00
SA dehumid regulator P-band setting.
102 | SA dehumid C-factor | 0.000 - 2.500
SA dehumid regulator affection setting.
103 | Dewpoint reg. P-band | 1.00 - 40.00 | PV 5.00
Dewpoint regulator P-band setting.
104 | Dewpoint reg. C-factor | 0.000 - 2.500
Dewpoint regulator affection setting.
105 | AYC chilled water temperature | 5.00-30.00°C
Setting of AYC chilled water temperature setpoint.
106 | Dewpoint neutralzone | 0.00-5.00°C
Dewpoint neutralzone setting.
107 | Comp. airflow | 0-30.00%
Setting of comp. airflow.
108 | Supply air-humidity | 10.00-90.00%
Setting of supply air-humidity.
109 | Water heating periodic op. time | 0-60min
Setting of periodic op. time (minute).
110 | Water heating interval | 0-168h
Setting of water heating intervall time (hour).
111 | P/C.HX. bypass adj. | -5.00-5.00°C | PV 2.02
Setting of plate/coil heat exchange bypass adjustment.
112 | EA/Room temperature com. | -55.00-125.00°C | PV 3.00
Setting of EA/Room temperature via communication.
113 | Outdoor temperature com. | -55.00-125.00°C | PV 3.00
Setting of outdoor temperature via communication.
114 | SA speed at fire. | 50.00-100.00% | PV 3.00
Setting of supply air speed at fire.
115 | EA speed at fire. | 50.00-100.00% | PV 3.00
Setting of extract air speed at fire.
116 | Temperature alarm setpoint. | -25.00-25.00°C | PV 3.00
Temperature alarm function setting (no.80).
117 | Supply air min P-band. | 1.00 - 40.00 | PV 3.00
Supply air min regulator P-band setting.
118 | Supply air min C-factor. | 0.000 - 2.500 | PV 3.00
Supply air min regulator affection setting.
119 | Supply air max P-band. | 1.00 - 40.00 | PV 3.00
Supply air max regulator P-band setting.
120 | Supply air max C-factor. | 0.000 - 2.500 | PV 3.00
Supply air max regulator affection setting.
121 | SA prefilter alarm limit. | 50-300Pa | PV 5.00
Supply air prefilter pressure alarm limit setting.
122 | EA prefilter alarm limit. | 50-300Pa | PV 5.00
Extract air prefilter pressure alarm limit setting.
123 | Xzone temperature reg. Neutral zone. | 0.50-10.00°C | PV 5.00
Xzone neutral zone setting before shift between heating and cooling.
124 | Xzone ERS 1 Diff. | 1.00 - 7.00°C | PV 5.00
Supply air temperature difference setting accordning to the diagram for Xzone ERS 1.
125 | Xzone ERS 1 Breakpoint. | 12.00 - 26.00°C | PV 5.00
Breakpoint setting accordning to the diagram for Xzone ERS 1.
126 | Xzone ERS 2 Breakpoint X1. | 10.00-38.00°C | PV 5.00
Breakpoint X1 setting accordning to the diagram for Xzone ERS 2.
127 | Xzone ERS 2 Breakpoint Y1. | 10.00-40.00°C | PV 5.00
Breakpoint Y1 setting accordning to the diagram for Xzone ERS 2.
128 | Xzone ERS 2 Breakpoint X2. | 11.00-39.00°C | PV 5.00
Breakpoint X2 setting accordning to the diagram for Xzone ERS 2.
129 | Xzone ERS 2 Breakpoint Y2. | 10.00-40.00°C | PV 5.00
Breakpoint Y2 setting accordning to the diagram for Xzone ERS 2.
130 | Xzone ERS 2 Breakpoint X3. | 12.00-40.00°C | PV 5.00
Breakpoint X3 setting accordning to the diagram for Xzone ERS 2.
131 | Xzone ERS 2 Breakpoint Y3. | 10.00-40.00°C | PV 5.00
Breakpoint Y3 setting accordning to the diagram for Xzone ERS 2.
132 | Xzone SA Temperature setpoint. | 10.00-40.00°C | PV 5.00
Xzone supply air temperature setting, for supply air temp regulation mode.
133 | Xzone EA/Room Temperature setpoint. | 10.00-30.00°C | PV 5.00
Xzone extract air/room temperature setting, for extract air/room temp regulation mode.
134 | Xzone SA Min temp setpoint. | 8.00-20.00°C | PV 5.00
Xzone supply air min.setpoint during EA/room regulation mode.
135 | Xzone SA Max temp setpoint. | 16.00-50.00°C | PV 5.00
Xzone supply air max.setpoint during EA/room regulation mode.
136 | Preheating setpoint. | -30.00-30.00°C | PV 5.00
Setting of preheating temperature setpoint.
137 | Xzone P-band. | 1.00-40.00 | PV 5.00
Xzone regulator P-band setting.
138 | Xzone SA reheat C-factor. | 0.000 - 2.500 | PV 5.00
Xzone supply air reheat regulator affection setting.
139 | Xzone SA cooling C-factor. | 0.000 - 2.500 | PV 5.00
Xzone supply air cooling regulator affection setting.
140 | Xzone EA reheat C-factor. | 0.000 - 2.500 | PV 5.00
Xzone extract air reheat regulator affection setting.
141 | Xzone EA cooling C-factor. | 0.000 - 2.500 | PV 5.00
Xzone extract air cooling regulator affection setting.
142 | Xzone SA min P-band. | 1.00 - 40.00 | PV 5.00
Xzone supply air min regulator P-band setting.
143 | Xzone SA min C-factor. | 0.000 - 2.500 | PV 5.00
Xzone supply air min regulator affection setting.
144 | Xzone SA max P-band. | 1.00 - 40.00 | PV 5.00
Xzone supply air max regulator P-band setting.
145 | Xzone SA max C-factor. | 0.000 - 2.500 | PV 5.00
Xzone supply air min regulator affection setting.
146 | Preheat P-band. | 1.00 - 40.00 | PV 5.00
Preheat regulator P-band setting.
147 | Preheat C-factor. | 0.000 - 2.500 | PV 5.00
Preheat regulator affection setting.
148 | ReCO2 CO2 setpoint. | 0-100.00% | PV 5.00
Setting of ReCO2 CO2 setpoint.
149 | ReCO2 min outdoor air. | 0-8200l/s | PV 5.00
Setting of ReCO2 min outdoor air.
150 | ReCO2 min exhaust air. | 0-8200l/s | PV 5.00
Setting of ReCO2 min exhaust air.
151 | ReCO2 CO2 P-band. | 1.00 - 100.00 | PV 5.00
ReCO2 CO2 regulator P-band setting.
152 | ReCO2 CO2 C-factor. | 0.000 - 5.000 | PV 5.00
ReCO2 CO2 regulator affection setting.
153 | ReCO2 CO2 flow C-factor. | 0.000 - 5.000 | PV 5.00
ReCO2 flow regulator affection setting.
154 | ReCO2 heating C-factor. | 0.000 - 5.000 | PV 5.00
ReCO2 heating regulator affection setting.
155 | ReCO2 cooling C-factor. | 0.000 - 5.000 | PV 5.00
ReCO2 heating regulator affection setting.
156 | AYC heat temp set. | 10.00-80.00°C | PV 5.07
Setting of AYC heated water temperature setpoint.
157 | AYC heat P-band. | 1.00 - 40.00 | PV 5.07
AYC heat regulator P-band setting.
158 | AYC heat C-factor. | 0.000 - 2.500 | PV 5.07
AYC heat regulator affection setting.
159 | AYC cool P-band. | 1.00 - 40.00 | PV 5.07
AYC cool regulator P-band setting.
160 | AYC cool C-factor. | 0.000 - 2.500 | PV 5.07
AYC cool regulator affection setting.
161 | AYC heat out comp. X1. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of heated water, outdoor temp X1 setting.
162 | AYC heat out comp. Y1. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of heated water, heated water temp Y1 setting.
163 | AYC heat out comp. X2. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of heated water, outdoor temp X2 setting.
164 | AYC heat out comp. Y2. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of heated water, heated water temp Y2 setting.
165 | AYC heat out comp. X3. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of heated water, outdoor temp X3 setting.
166 | AYC heat out comp. Y3. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of heated water, heated water temp Y3 setting.
167 | AYC heat room comp. temp limit. | 0.00-40.00°C | PV 5.07
AYC room compensation of heated water, heated water temp limit setting.
168 | AYC heat room comp P-band. | 1.00-10.00°C | PV 5.07
AYC room compensation of heated water, heated water P-band setting.
169 | AYC heat night comp temp. | -10.00-10.00°C | PV 5.07
AYC night compensation of heated water, heated water night setting.
170 | AYC heat pump on temp. | -40.00-40.00°C | PV 5.07
AYC pump operation of heated water, outdoor temp start setting.
171 | AYC heat pump off temp. | -40.00-40.00°C | PV 5.07
AYC pump operation of heated water, outdoor temp stop setting.
172 | AYC cool out comp. X1. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of chilled water, outdoor temp X1 setting.
173 | AYC cool out comp. Y1. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of chilled water, chilled water temp Y1 setting.
174 | AYC cool out comp. X2. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of chilled water, outdoor temp X2 setting.
175 | AYC cool out comp. Y2. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of chilled water, chilled water temp Y2 setting.
176 | AYC cool out comp. X3. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of chilled water, outdoor temp X3 setting.
177 | AYC cool out comp. Y3. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of chilled water, chilled water temp Y3 setting.
178 | AYC cool room comp. temp limit. | 0.00-40.00°C | PV 5.07
AYC room compensation of chilled water, chilled water temp limit setting.
179 | AYC cool room comp. P-band. | 1.00-10.00°C | PV 5.07
AYC room compensation of chilled water, chilled water P-band setting.
180 | AYC cool night comp temp. | -10.00-10.00°C | PV 5.07
AYC night compensation of chilled water, chilled water night setting.
181 | AYC cool pump on temp. | -40.00-40.00°C | PV 5.07
AYC pump operation of chilled water, outdoor temp start setting.
182 | AYC cool pump off temp. | -40.00-40.00°C | PV 5.07
AYC pump operation of chilled water, outdoor temp stop setting.
183 | Humid reg. Start. | 10.00-90.00% | PV 5.10
Humidifying start limit setting.
184 | Humid reg. Stop. | 15.00-95.00% | PV 5.10
Humidifying stop limit setting.

## Binary Out
GB.Metasys.100915
Binary Output (BO).1bit (R/W).
N2 Idx | Name | Min/Max | Misc
1 | Alarm reset | 0-1
Resets tripped alarms.
2 | SA Boosting func. | 0-1
Setting for activating the boost function for the supply air fan.
3 | EA Boosting func. | 0-1
Setting for activating the boost function for the extract air fan.
4 | R.HX. Defrost func. | 0-1
Setting for activating the defrost function for the rotary heat exchanger.
5 | SA Down regulation func. | 0-1 | PV 3.00
Setting for activating the down regulation function for the supply air fan. (Moved to ADI 128 in PV 3.00)
6 | Reserve
7 | Reserve
8 | Cool operation mode | 0-1
Setting for cooling between off and auto operation.
9 | Int. Night heat func. | 0-1
Setting for activating the intermittent night heat function.
10 | Damper func. | 0-1
Setting for activating the damper output relay during int. night heat.
11 | Summer night cooling | 0-1
Setting for activating the suumer night cool function.
12 | Temp displacement | 0-1
Setting for activating the external temperature displacement function.
13 | Outdoor temp compensation | 0-1
Setting for activating the outdoor temperature compensation function.
14 | Outdoor airflow compensation | 0-1
Setting for activating the outdoor airflow compensation function.
15 | Auto. Summer/winter switch | 0-1
Setting for activating the automatic switch between ummer/winter time function.
16 | Switch clock func. | 0-1
Setting for switch clock function type. 0=Stop - low speed - high speed. 1=Low speed - high speed.
17 | Internal fire alarm func. | 0-1
Setting for activating the internal fire alarm function.
18 | EA at fire | 0-1 | PV 3.00
Setting for activating the extract air fan operation at fire function. (Moved to ADI 127 in PV 3.00)
19 | External alarm 1 active at closure | 0-1
Setting for external alarm number 1 condition to be activated. 0= alarm at closed input. 1= alarm at open input.
20 | External alarm 2 active at closure | 0-1
Setting for external alarm number 2 condition to be activated. 0= alarm at closed input. 1= alarm at open input.
21 | Reserve
22 | Dewpoint reg. func. | 0-1
Setting for activating the dewpoint regulator funktion.
23 | Dehumid reg. func. | 0-1
Setting for activating the dehumid regulator funktion.
24 | External fire alarm func. | 0-1 | PV 3.00
Setting for external fire resetting function. 0= Manual. 1= Automatic.
25 | External alarm 1 func. | 0-1 | PV 3.00
Setting for external alarm 1 resetting function. 0= Manual. 1= Automatic.
26 | External alarm 2 func. | 0-1 | PV 3.00
Setting for external alarm 2 resetting function. 0= Manual. 1= Automatic.
27 | Temperature alarm func. | 0-1 | PV 3.00
Setting for activating temperature below setpoint alarm function (no.80).
28 | Int. Night heat output func. | 0-1 | PV 5.00
Setting for selecting the intermittent night heat output function. 0=IQnomic 1=IQnomic+
29 | AYC heat out comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC outdoor comp. heated water function. 0=Inactive 1=Active
30 | AYC heat room comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC room comp. heated water function. 0=Inactive 1=Active
31 | AYC heat room comp. night block func. | 0-1 | PV 5.07
Setting for selecting the AYC room comp. heated water night block function. 0=Inactive 1=Active
32 | AYC heat night comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC night comp. heated water function. 0=Inactive 1=Active
33 | AYC heat valve signal func. | 0-1 | PV 5.07
Setting for selecting the AYC valve signal heated water alarm function. 0=Inactive 1=Active
34 | AYC cool out comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC outdoor comp. chilled water function. 0=Inactive 1=Active
35 | AYC cool room comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC room comp. chilled water function. 0=Inactive 1=Active
36 | AYC cool room comp. night block func. | 0-1 | PV 5.07
Setting for selecting the AYC room comp. chilled water night block function. 0=Inactive 1=Active
37 | AYC cool night comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC night comp. chilled water function. 0=Inactive 1=Active
38 | AYC cool valve signal func. | 0-1 | PV 5.07
Setting for selecting the AYC valve signal chilled water alarm function. 0=Inactive 1=Active