## Overview_data
GB.BACnet480.100129
BACnet IP
Compact/GOLD LP, program version 2.01 and newer versions.
Overview
This BACnet driver is implemented in Compact/GOLD LP PV2.01 and provides the function
of monitoring and operating the air handling unit.
Compact/GOLD LP is a BACnet Application Specific Controller (B-ASC).
The supported Data Link Layer Options are BACnet / IP.
See also document BACnet PICS (Protocol Implementation Conformance Statement)
and EDE (Engineering Data Exchange).
BACnet Interoperability Building Blocks Supported.
Data Sharing |  | DS-RP-B | Data Sharing-Read Property-B
Data Sharing |  | DS-WP-B | Data Sharing-Write Property-B
Data Sharing |  | DS-COV-B | Data Sharing-COV-B
Device Management |  | DM-DDB-B | Device Management-Dynamic Device Binding-B
Device Management |  | DM-DOB-B | Device Management-Dynamic Object Binding-B
Device Management |  | DM-DCC-B | Device Management-Dynamic Communication Control-B
Standard Object Types Supported.
Object Type | _
Analog Input | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Units, Min_Pres_Value, Max_Pres_Value, Resolution, COV_Increment.
Analog Value | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Units, Priority_Array, Relinquish_Default, COV_Increment.
Binary Input | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Polarity.
Binary Value | Object_Identifier, Object_Name, Object_Type, Present_Value, Status_Flags, Event_State, Out_Of_Service, Priority_Array, Relinquish_Default.
Device | Object_Identifier, Object_Name, Object_Type, System_Status, Vendor_Name, Vendor_Identifier, Model_Name, Firmware_Revision, Application_Software_Version, Location, Description, Protocol_Version, Protocol_Revision, Protocol_Services_Supported, Protocol_Object_Types_Supported, Object_List, Max_APDU_Length_Accepted, Segmentation_Supported, APDU_Timeout, Number_Of_APDU_Retries, Device_Address_Binding, Database_Revision, Active_COV_Subscriptions.

## Overview parameters
GB.BACnet480.100129
Operation mode 1 |  | AI 84 |  | Extract air filter pressure level |  | AI 52 |  | EA/Room temperature |  | AI 28
Communication operation mode |  | AV 174 |  | EA filter pressure level limit |  | AI 53 |  | EA/Room temperature setpoint |  | AV 41
Operation mode 2 |  | AI 85 | [5 empty] | SA Min temperature setpoint |  | AV 42
Operation output |  | BI 7 | [5 empty] | SA Max temperature setpoint |  | AV 43
Low speed output |  | BI 3 |  |  | EA Duct pressure |  | AI 6
High speed output |  | BI 4 |  |  | EA Low speed pressure setpoint |  | AV 12
Damper output |  | BI 8 |  |  | EA High speed pressure setpoint |  | AV 13 | SA Duct Pressure |  | AI 4
Present tripped alarm |  | AI 78 | [5 empty] | SA Low speed pressure setpoint |  | AV 8
A-alarm |  | BI 5 | [5 empty] | SA High speed pressure setpoint |  | AV 9
B-alarm |  | BI 6
Alarm reset |  | BV 0
[8 empty] | SA Temperature |  | AI 27
[8 empty] | SA Temperature setpoint |  | AV 40
EA Airflow |  | AI 2 | [5 empty] | ERS 1 Diff |  | AV 32
EA Fan level |  | AI 13
EA Low speed airflow setpoint |  | AV 4
EA High speed airflow setpoint |  | AV 5
Outdoor temperature |  | AI 29
Supply air filter pressure level |  | AI 49
SA filter pressure level limit |  | AI 50
Heat exchange regulator |  | AI 90
| SA Airflow |  | AI 0 |  | Reheat level |  | AI 36 | Cooling level |  | AI 39
| SA Fan level |  | AI 12 |  | Heat output |  | BI 0 | Cool output 1 |  | BI 1
| SA Low speed airflow setpoint |  | AV 0 |  | Anti frost temperature |  | AI 32 | Cool output 2 |  | BI 2
| SA High speed airflow setpoint |  | AV 1

## Analog Inputs
GB.BACnet480.100129
Analog Inputs (RO).
Object Instance | Object Name | Min/Max
0 | SA Airflow | 0-1000l/s
Present supply airflow.
1 | SA Airflow regulator | 0-1000l/s
Present supply airflow regulator setpoint.
2 | EA Airflow | 0-1000l/s
Present extract airflow.
3 | EA Airflow regulator | 0-1000l/s
Present extract airflow regulator setpoint.
4 | SA Duct pressure | 0-2000Pa
Present supply air duct pressure.
5 | SA Duct pressure regulator | 0-2000Pa
Present supply air duct pressure regulator setpoint.
6 | EA Duct pressure | 0-2000Pa
Present extract air duct pressure.
7 | EA Duct pressure regulator | 0-2000Pa
Present extract air duct pressure regulator setpoint.
8 | Reserve
9 | SA VAV demand regulator | 0-100.00%
Present supply air VAV demand regulator setpoint.
10 | Reserve
11 | EA VAV demand regulator | 0-100.00%
Present extract air VAV demand regulator setpoint.
12 | SA Fan level | 0-100.00%
Present running level for the supply air fan.
13 | EA Fan level | 0-100.00%
Present running level for the extract air fan.
14 | SA Fan effect | 0-500W
Present power consumption level for the supply air fan.
15 | EA Fan effect | 0-500W
Present power consumption level for the extract air fan.
16 | SFP | 0.0-9.9
SFP supply air + extract air.
17 | Reserve
18 | Reserve
19 | SA Voltage | 0-500V
Present voltage level for the supply air fan.
20 | EA Voltage | 0-500V
Present voltage level for the extract air fan.
21 | SA Current | 0-2.000A
Present current level for the supply air fan.
22 | EA Current | 0-2.000A
Present current level for the extract air fan.
23 | SA Airflow pressure | 0-2000Pa
Present airflow pressure in the supply air fan inlet.
24 | EA Airflow pressure | 0-2000Pa
Present airflow pressure in the extract air fan inlet.
25 | SA Temp regulator | -55.00-125.00°C
Present supply air temperature regulator setpoint.
26 | EA Temp regulator | -55.00-125.00°C
Present extract air temperature regulator setpoint.
27 | SA Temperature | -55.00-125.00°C
Present supply air temperature.
28 | EA/Room temperature | -55.00-125.00°C
Present extract air/room temperature in the unit.
29 | Outdoor temperatur | -55.00-125.00°C
Present outdoor air temperature in the unit.
30 | EA/Room temperature (external) | -55.00-125.00°C
Present room temperature external from the unit.
31 | Outdoor temperatur (external) | -55.00-125.00°C
Present outdoor air temperature external from the unit.
32 | Anti frost temperature | -55.00-125.00°C
Present anti frost temperature for water reheating coils.
33 | Reserve
34 | Reserve
35 | Rotary heat exchanger level | 0-100.00%
Present operation level from rotary heat exchanger.
36 | Reheat level | 0-100.00%
Present level of reheat.
37 | SA Down regulation level | 0-100.00%
Present level of supply airflow down regulation.
38 | Reserve
39 | Cooling level | 0-100.00%
Present level of cooling.
40 | Heating boost level | 0-100.00%
Present level of heating boost.
41 | Cooling boost level | 0-100.00%
Present level of cooling boost.
42 | HX pressure level | 0-2000Pa
Present pressure drop for the rotary heat exchanger.
43 | HX pressure alarm limit | 0-2000Pa
Present pressure drop alarm limit for the rotary heat exchanger.
44 | HX temperature | 0-100.00°C
Present temperature inside the control unit for the rotary heat exchanger.
45 | Effect reduction level | 0-100.00%
Present level of max output signal for electrical reheaters, active during low supply airflow.
46 | Anti frost temp setpoint/operation | 10.00-16.00°C
Present anti frost temperature setpoint for water reheating coils during unit operation.
47 | Anti frost temp setpoint/stop | 15.00-40.00°C
Present anti frost temperature setpoint for water reheating coils when the unit is in stop.
48 | Anti frost temp alarm limit | 5.00-30.00°C
Setting of antifrost temperature alarm limit.
49 | Supply air filter pressure level | 0-2000Pa
Present supply air filter pressure drop.
50 | Supply air filter pressure alarm limit. | 0-2000Pa
Present supply air filter pressure alarm limit.
51 | Supply air filter pressure level, new | 0-2000Pa
Supply air filter pressure saved from calibration.
52 | Extract air filter pressure level | 0-2000Pa
Present extract air filter pressure drop.
53 | Extract air filter pressure alarm limit. | 0-2000Pa
Present extract air filter pressure alarm limit.
54 | Extract air filter pressure level, new | 0-2000Pa
Extract air filter pressure saved from calibration.
55 | Reserve
56 | Coil type | 0-20
Present connected reheat coil type.
57 | Cool step time | 0-600s
Present time between cool step shift.
58 | Cool relay 1 restart time | 0-900s
Present time between two starts of cool relay 1.
59 | Cool relay 2 restart time | 0-900s
Present time between two starts of cool relay 2.
60 | Programversion, HMI | 0-10.00
Present programversion for the handterminal.
61 | Programversion, HMI-slave | 0-10.00
Present programversion for the extra handterminal.
62 | Programversion, main controller. | 0-10.00
Present programversion for the main control unit.
63 | Programversion, SA FC-1. | 0-10.00
Present programversion for the supply air frequency converter no.1.
64 | Programversion, SA FC-2. | 0-10.00
Present programversion for the supply air frequency converter no.2.
65 | Programversion, EA FC-1. | 0-10.00
Present programversion for the extract air frequency converter no.1.
66 | Programversion, EA FC-2. | 0-10.00
Present programversion for the extract air frequency converter no.2.
67 | Programversion, HX control unit | 0-10.00
Present programversion for the rotary heat exchange control unit.
68 | Weekday | 0 - 6
Present weekday for the unit's internal clock.
69 | Extended low speed op. Hours | 0-23
Present time for extended low speed operation.
70 | Extended low speed op. Minutes | 0-59
Present time for extended low speed operation.
71 | Extended high speed op. Hours | 0-23
Present time for extended high speed operation.
72 | Extended high speed op. Minutes | 0-59
Present time for extended high speed operation.
73 | SA Fan operation time | 0-9999
Present operation time for the supply air fan, measured in minutes and present in days (24h).
74 | EA Fan operation time | 0-9999
Present operation time for the extract air fan, measured in minutes and present in days (24h).
75 | Cool operation time | 0-9999
Present operation time for cooling, measured in minutes and present in days (24h).
76 | Heat exchange operation time | 0-9999
Present operation time for heat exchange, measured in minutes and present in days (24h).
77 | Reheat operation time | 0-9999
Present operation time for reheat, measured in minutes and present in days (24h).
78 | Present tripped alarm | 0-200
Present tripped alarm number with highest priority.
79 | Active not tripped alarm no.1 | 0-200
Present active alarm in delay.
80 | Active not tripped alarm no.2 | 0-200
Present active alarm in delay.
81 | Active not tripped alarm no.3 | 0-200
Present active alarm in delay.
82 | SA Fan size | 02 - 08
Present supply air fan size.
83 | EA Fan size | 02 - 08
Present extract air fan size.
84 | Operation mode 1 | 0 - 18
0=Manual stop. 1=Ext. stop. 2=Com. stop 1. 3=Manual high speed. 4=Summer night cooling. 5=Int. night heat. 6=Manual low speed. 7=Ext. high speed. 8=Com. high speed. 9=Year channel stop. 10=Year channel high speed. 11=Year channel low speed. 12=Time channel high speed. 13=Ext. low speed. 14=Com. low speed. 15=Time channel low speed. 16=Time channel stop. 17=Low speed=stop. 18=Com. stop 2.
85 | Operation mode 2 | 0 - 24
0= 1=Coold air recovery. 2=Cooling boost. 3=SA down regulation. 4=HX defrosting. 5=Anti frost func. active. 6=Effect reduction. 7=Startup. 8=Zero calibration. 9=Extended low speed. 10=Extended high speed. 11=Air adjustment. 12=Cooling off. 13=Purging R.HX. 14=Extended R.HX. op. 15=Filter calibration. 16=R.HX. calibration 17=Morning boost. 18=Heating boost. 19=Alarm. 20=Cooling pressure reduction. 21=Startup extract air fan. 22=Reserve. 23=Airing. 24=Heating.
86 | Operation mode, manual | 0 - 3
Present manual operation set on the unit's handterminal. 0=Stop. 1=Auto operation. 2=Manual low speed. 3=Manual high speed.
87 | Copy of Input Status 1-16. | 0-65535
Bit 0=1x0001 Bit 1=1x0002 Bit 15=1x0016
88 | Copy of Input Status 17-32. | 0-65535
Bit 0=1x00017 Bit 1=1x00018 Bit 15=1x0032
89 | Copy of Input Status 33-48. | 0-65535
Bit 0=1x00033 Bit 1=1x00034 Bit 15=1x0048
90 | Heat exchanger regulator | 0-100.00%
Present level of heat exchanger regulator.
91 | Extract air-humidity | 0-100.00%
Present level of extract air-humidity.
92 | Extract air-humidity temperature | -55.00-125.00°C
Present temperature inside extract air-humidity sensor.
93 | Extract air-dewpoint | -55.00-125.00°C
Calculated extract air-dewpoint.
94 | AYC chilled water temperature | -55.00-125.00°C
Present AYC chilled water temperature.
95 | AYC chilled water temperature regulator | -55.00-125.00°C
Present AYC chilled water temperature regulator setpoint.
96 | AYC chilled water output | 0-100.00%
Present level of AYC chilled water valve output.
97 | Supply air-dewpoint regulator | -55.00-125.00°C
Present supply air-dewpoint regulator setpoint.
98 | Supply air-humidity | 0-100.00%
Present level of supply air-humidity
99 | Supply air-humidity temperature | -55.00-125.00°C
Present temperature inside supply air-humidity sensor.
100 | Supply air-dewpoint | -55.00-125.00°C
Calculated supply air-dewpoint.
101 | Reserve
102 | Reserve
103 | Reserve
104 | Reserve
105 | R.HX. Efficiency | 0-100.00%
Calculated level of rotary heat exchanger efficiency.
106 | Reserve
107 | Reserve
108 | Supply air prefilter pressure level | 0-2000Pa
Present supply air prefilter pressure drop.
109 | Supply air prefilter pressure alarm limit. | 0-2000Pa
Present supply air prefilter pressure alarm limit.
110 | Supply air prefilter pressure level, new | 0-2000Pa
Supply air prefilter pressure saved from calibration.
111 | Extract air prefilter pressure level | 0-2000Pa
Present extract air prefilter pressure drop.
112 | Extract air prefilter pressure alarm limit. | 0-2000Pa
Present extract air prefilter pressure alarm limit.
113 | Extract air prefilter pressure level, new | 0-2000Pa
Extract air prefilter pressure saved from calibration.
114 | Reserve
115 | Reserve
116 | Reserve
117 | Reserve
118 | Reserve
119 | Reserve
120 | Reserve
121 | Reserve
122 | Reserve
123 | Reserve
124 | Pre-heating air temperature | -55.00-125.00°C
Present pre-heating air temperature.
125 | Pre-heating level | 0-100.00%
Present level of pre-heating.
126 | Pre-heating anti frost temperature | -55.00-125.00°C
Present anti frost temperature for water pre-heating coils.
127 | Reserve
128 | Reserve
129 | Reserve
130 | Reserve
131 | Reserve
132 | Reserve
133 | Preheat operation time | 0-9999
Present operation time for preheat, measured in minutes and present in days (24h).
134 | Reserve
135 | Reserve
136 | Demand VOC Level | 0-100.00%
Present level of demand VOC input.
137 | Demand Vin Level | 0-100.00%
Present level of demand 0-10VDC input.
138 | SA Filter level calculated | 0-100.00%
Present level of calculated supply air filter.
139 | EA Filter level calculated | 0-100.00%
Present level of calculated extract air filter.
140 | AYC heat temperature | -55.00-125.00°C
Present AYC heat temperature.
141 | AYC heat temp regulator | -55.00-125.00°C
Present AYC heat temperature regulator setpoint.
142 | AYC heat valve output | 0-100.00%
Present level of AYC heat valve output.

## Analog Value
GB.BACnet480.100129
Analog Value (R/W).
Object Instance | Object Name | Min/Max
0 | SA Low speed airflow setpoint | 0-1000l/s
Supply airflow setpoint for the unit when running in low speed operation.
1 | SA High speed airflow setpoint | 0-1000l/s
Supply airflow setpoint for the unit when running in high speed operation.
2 | SA Max speed airflow setpoint | 0-1000l/s
Supply airflow max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
3 | SA Min speed airflow setpoint | 0-1000l/s
Supply airflow min. limit for the unit when the low/high speed operation setpoint is altered when running in fan regulation mode VAV demand.
4 | EA Low speed airflow setpoint | 0-1000l/s
Extract airflow setpoint for the unit when running in low speed operation.
5 | EA High speed airflow setpoint | 0-1000l/s
Extract airflow setpoint for the unit when running in high speed operation.
6 | EA Max speed airflow setpoint | 0-1000l/s
Extract airflow max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
7 | EA Min speed airflow setpoint | 0-1000l/s
Extract airflow min. limit for the unit when the low/high speed operation setpoint is altered when running in fan regulation mode VAV demand.
8 | SA Low speed pressure setpoint | 0-750Pa
Supply air duct pressure setpoint for the unit when running in low speed operation.
9 | SA High speed pressure setpoint | 20-750Pa
Supply air duct pressure for the unit when running in high speed operation.
10 | SA Max speed output signal | 10.00-100.00%
Max. limit for the supply air fan speed when running in pressure regulation mode.
11 | SA Max speed pressure setpoint | 20-750Pa
Supply air duct pressure max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
12 | EA Low speed pressure setpoint | 0-750Pa
Extract air duct pressure setpoint for the unit when running in low speed operation.
13 | EA High speed pressure setpoint | 20-750Pa
Extract air duct pressure setpoint for the unit when running in high speed operation.
14 | EA Max speed output signal | 10.00-100.00%
Max. limit for the extract air fan speed when running in pressure regulation mode.
15 | EA Max speed pressure setpoint | 20-750Pa
Extract air duct pressure max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
16 | SA Low speed demand setpoint | 0-100.00%
Supply air setpoint for the 0-10V input signal on terminal 35..37 for the unit when running in low speed operation.
17 | SA High speed demand setpoint | 0-100.00%
Supply air setpoint for the 0-10V input signal on terminal 35..37 for the unit when running in high speed operation.
18 | EA Low speed demand setpoint | 0-100.00%
Extract air setpoint for the 0-10V input signal on terminal 35..37 for the unit when running in low speed operation.
19 | EA High speed demand setpoint | 0-100.00%
Extract air setpoint for the 0-10V input signal on terminal 35..37 for the unit when running in high speed operation.
20 | SA Airflow regulation zone | 1.00 - 10.00
Supply airflow regulation zone setting in % of the present airflow setpoint that the regulator is allowed to work within.
21 | SA Airflow C-factor | 0.005 - 2.500
Supply airflow regulator affection setting.
22 | EA Airflow regulation zone | 1.00 - 10.00
Extract airflow regulation zone setting in % of the present airflow setpoint that the regulator is allowed to work within.
23 | EA Airflow C-factor | 0.005 - 2.500
Extract airflow regulator affection setting.
24 | SA Pressure regulation zone | 1.00 - 10.00
Supply air pressure regulation zone setting in % of the present duct pressure setpoint that the regulator is allowed to work within.
25 | SA Pressure C-factor | 0.005 - 2.500
Supply air pressure regulator affection setting.
26 | EA Pressure regulation zone | 1.00 - 10.00
Extract air pressure regulation zone setting in % of the present duct pressure setpoint that the regulator is allowed to work within.
27 | EA Pressure C-factor | 0.005 - 2.500
Extract air pressure regulator affection setting.
28 | SA Demand P-band. | 1.00 - 100.00
Supply air demand regulator P-band setting.
29 | SA Demand C-factor | 0.005 - 2.500
Supply air demand regulator affection setting.
30 | EA Demand P-band. | 1.00 - 100.00
Extract air demand regulator P-band setting.
31 | EA Demand C-factor | 0.005 - 2.500
Extract air demand regulator affection setting.
32 | ERS 1 Diff | 1.00 - 7.00°C
Supply air temperature difference setting accordning to the diagram for ERS 1.
33 | ERS 1 Breakpoint | 12.00 - 26.00°C
Breakpoint setting accordning to the diagram for ERS 1.
34 | ERS 2 Breakpoint X1 | 10.00-38.00°C
Breakpoint X1 setting accordning to the diagram for ERS 2.
35 | ERS 2 Breakpoint Y1 | 10.00-40.00°C
Breakpoint Y1 setting accordning to the diagram for ERS 2.
36 | ERS 2 Breakpoint X2 | 11.00-39.00°C
Breakpoint X2 setting accordning to the diagram for ERS 2.
37 | ERS 2 Breakpoint Y2 | 10.00-40.00°C
Breakpoint Y2 setting accordning to the diagram for ERS 2.
38 | ERS 2 Breakpoint X3 | 12.00-40.00°C
Breakpoint X3 setting accordning to the diagram for ERS 2.
39 | ERS 2 Breakpoint Y3 | 10.00-40.00°C
Breakpoint Y3 setting accordning to the diagram for ERS 2.
40 | SA Temperature setpoint | 10.00-40.00°C
Supply air temperature setting, for supply air temp regulation mode.
41 | EA/Room Temperature setpoint | 10.00-40.00°C
Extract air/room temperature setting, for Extract air/room temp regulation mode.
42 | SA Min temp setpoint | 8.00-20.00°C
Supply air min.setpoint during EA/room regulation mode.
43 | SA Max temp setpoint | 16.00-50.00°C
Supply air max.setpoint during EA/room regulation mode.
44 | SA Temperature P-band | 1.00 - 40.00
Supply air temperature regulator P-band setting.
45 | EA/Room Temperature P-band | 1.00 - 40.00
Extract air/room temperature regulator P-band setting.
46 | SA HX. Reg C-factor | 0.000 - 2.500
Supply air heat exchange regulator affection setting.
47 | EA/Room HX. Reg C-factor | 0.000 - 2.500
Extract air/room heat exchange regulator affection setting.
48 | SA Heat Reg C-factor | 0.000 - 2.500
Supply air reheat regulator affection setting.
49 | EA/Room Heat Reg C-factor | 0.000 - 2.500
Extract air/room reheat regulator affection setting.
50 | Reserve
51 | Reserve | 0.000 - 2.500
52 | Reserve | 0.000 - 2.500
53 | Reserve | 0.000 - 2.500
54 | SA Down regulation Reg C-factor | 0.000 - 2.500
Supply air reheat regulator affection setting.
55 | Reserve
56 | SA Cool reg C-factor | 0.000 - 2.500
Supply air cool regulator affection setting.
57 | EA/Room Cool reg C-factor | 0.000 - 2.500
Extract air/room cool regulator affection setting.
58 | SA Cooling boost C-factor | 0.000 - 2.500
Supply air cooling boost affection setting.
59 | EA/Room Cooling boost reg C-factor | 0.000 - 2.500
Extract air/room cooling boost regulator affection setting.
60 | HX Pressure alarm set. | 30 - 100Pa
Heat exchange pressure alarm limit setting (alarm no.38).
61 | Reserve
62 | Reserve
63 | Cooling off set. | 10 - 50%
Cooling off airflow setting in % of max. airflow.
64 | SA Down regulation neautral zone | 0.00-10.00°C
Neutral zone setting before downregulation is permitted.
65 | Cool Outdoor temp limit.1 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 1.
66 | Cool Outdoor temp limit.2 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 2.
67 | Cool Outdoor temp limit.3 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 3.
68 | Temperature reg. Neutral zone | 0.50-10.00°C
Neutral zone setting before shift between heating and cooling.
69 | SA Cool min air flow | 0-1000l/s
Supply air min. air flow setting for cooling.
70 | EA Cool min air flow | 0-1000l/s
Extract air min. air flow setting for cooling.
71 | Heating boost start limit | 2.00-10.00°C
Heating boost start temperature limit.
72 | Cooling boost start limit | 2.00-10.00°C
Cooling boost (comfort) start temperature limit.
73 | SA Filter alarm limit | 0-1000Pa
Supply air filter pressure alarm limit setting.
74 | EA Filter alarm limit | 0-1000Pa
Extract air filter pressure alarm limit setting.
75 | Int. Night heat room start temp | 5.00-40.00°C
Intermittent night heat function, extract air temperature setting for start.
76 | Int. Night heat room stop temp | 5.00-40.00°C
Intermittent night heat function, extract air temperature setting for stop.
77 | Int. Night heat SA temp setpoint | 5.00-40.00°C
Intermittent night heat function, supply air temperature setpoint during night heat.
78 | Int. Night heat SA airflow setpoint | 0-1000l/s
Intermittent night heat function, supply airflow setpoint during night heat.
79 | Int. Night heat EA airflow setpoint | 0-1000l/s
Intermittent night heat function, extract airflow setpoint during night heat.
80 | Summer night cool EA start temp | 17.00-27.00°C
Summer night cool function, extract air temperature setting for start.
81 | Summer night cool EA stop temp | 12.00-22.00°C
Summer night cool function, extract air temperature setting for stop.
82 | Summer night cool outdoor temp limit | 5.00-15.00°C
Summer night cool function, outdoor temperature limit.
83 | Summer night cool SA temp setpoint | 10.00-20.00°C
Summer night cool function, supply air temperature setpoint during summer night cool.
84 | Outdoor temp comp. Winter X1. | -30.00-(-10.00)°C
Endpoint of winter compensation.
85 | Outdoor temp comp. Winter X2. | -10.00-15.00°C
Startpoint of winter compensation.
86 | Outdoor temp comp. Winter Y1. | 0.00-10.00°C
Level of winter compensation at X1.
87 | Outdoor temp comp. Summer X3. | 15.00-25.00°C
Startpoint of summer compensation.
88 | Outdoor temp comp. Summer X4. | 25.00-40.00°C
Endpoint of summer compensation.
89 | Outdoor temp comp. Summer Y2. | -10.00-10.00°C
Level of summer compensation at X4.
90 | Outdoor airflow comp. Winter X1. | -30.00-(-10.00)°C
Endpoint of winter compensation.
91 | Outdoor airflow comp. Winter X2. | -10.00-15.00°C
Startpoint of winter compensation.
92 | Outdoor airflow comp. Winter Y1. | 0-50.00%
Level of airflow compensation at X1.
93 | Reserve
94 | EA/Room min temp alarm limit | 8.00-20.00°C
Setting for min extract air /room temp alarm no.40.
95 | SA Deviation alarm limit | 2.00-15.00°C
Setting for supply air temperature below present setpoint, alarm no.41.
96 | Reserve
97 | SA Fan regulation mode | 0 - 3
Setting of regulation type for the supply air fan. 0=Airflow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by EA fan.
98 | EA Fan regulation mode | 0 - 3
Setting of regulation type for the extract air fan. 0=Airflow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by SA fan.
99 | ERS Step | 1 - 4
Setting of curve when temperature is above breakpoint.
100 | Temperature regulation mode. | 0 - 3
Setting of temperature regulation type. 0=ERS 1 reg. 1=ERS 2 reg. 2=SA reg. 3=EA/Room reg.
101 | Cooling off periode | 60 - 1500s
Time setting for cooling off electrical heating coil.
102 | Cool step time | 0 - 600s
Time setting between cool step shift.
103 | Cool restart time | 60 - 900s
Setting of time between two starts of the cool relays.
104 | Cool regulation mode | 0 - 4
Setting of cool regulation type 0=Controlled 0-10V 1=Controlled 10-0V 2=On/Off 1-step 3=On/Off 2-steps 4=On/Off 3-steps binary
105 | Heating boost regulation mode. | 0 - 1
Setting for heating boost function. 0=Inactive. 1=Active.
106 | Cooling boost regulation mode. | 0 - 5
Setting of cooling boost regulation type. 0=Inactive. 1=Comfort. 2=Economy. 3=Sequence. 4=Comfort+economy. 5=Economy+sequence.
107 | Filter calibration mode | 0 - 4
Setting for required filter calibration. 0=Inactive. 1=SA+EA-Filter. 2=SA-Filter. 3=EA-Filter. 4=HX.
108 | Air adjustment time, minutes | 0 - 1728
Setting for amount of minutes to air adjustment function.
109 | Air adjustment time, hours | 0 - 72
Setting for amount of hours to air adjustment function.
110 | Handterminal language | 0 - 18
0=Svenska 1=Norsk 2=Dansk 3=Suomi 4=English 5=Français 6=Deutsch 7=Polski 8=Český 9=Italiano 10=Español 11=Português 12=Pycckий 13=Eesti 14=Latviesu 15=Lietiviu 16=Nederlands 17=Magyar 18=Türkçe
111 | Summer night cool start, hour | 0-23
Setting for start time of summer night cooling function.
112 | Summer night cool start, minute | 0-59
Setting for start time of summer night cooling function.
113 | Summer night cool stop, hour | 0-23
Setting for stop time of summer night cooling function.
114 | Summer night cool stop, minute | 0-59
Setting for stop time of summer night cooling function.
115 | Reserve
116 | Reserve
117 | Morning boost time, hours | 0-23
Setting of morning boost time before normal operation.
118 | Morning boost time, minutes | 0-59
Setting of morning boost time before normal operation.
119 | Startup time | 0 - 600s
Setting of time for startup when the unit regulator is running with fixed signals.
120 | Start delay SA fan. | 0 - 600s
Setting of start delay time for the supply air fan.
121 | Start delay EA fan. | 0 - 600s
Setting of start delay time for the extract air fan after supply air fan has started.
122 | Air flow unit | 0 -2
Setting of air flow unit presented in the unit's handterminal and WEB. 0=l/s. 1=m3/s. 2=m3/h.
123 | Reserve
124 | Year | 2000-2099
Setting for the unit's internal clock.
125 | Month | 1-12
Setting for the unit's internal clock.
126 | Date | 0-31
Setting for the unit's internal clock.
127 | Hour | 0-23
Setting for the unit's internal clock.
128 | Minute | 0-59
Setting for the unit's internal clock.
129 | Second | 0-59
Setting for the unit's internal clock.
130 | Time channel 1 status | 0-10,16-26
Low speed High speed 0=Inactive 16=Inactive 1=Monday 17=Monday 2=Tuesday 18=Tuesday 3=Wednesday 19=Wednesday 4=Thursday 20=Thursday 5=Friday 21=Friday 6=Saturday 22=Saturday 7=Sunday 23=Sunday 8=Monday..Friday 24=Monday..Friday 9=Monday..Sunday 25=Monday..Sunday 10=Saturday..Sunday 26=Saturday..Sunday
131 | Time channel 1 start hour | 0-23
132 | Time channel 1 start minute | 0-59
133 | Time channel 1 stop hour | 0-23
134 | Time channel 1 stop minute | 0-59
135 | Time channel 2 status | 0-10,16-26
136 | Time channel 2 start hour | 0-23
137 | Time channel 2 start minute | 0-59
138 | Time channel 2 stop hour | 0-23
139 | Time channel 2 stop minute | 0-59
140 | Time channel 3 status | 0-10,16-26
141 | Time channel 3 start hour | 0-23
142 | Time channel 3 start minute | 0-59
143 | Time channel 3 stop hour | 0-23
144 | Time channel 3 stop minute | 0-59
145 | Time channel 4 status | 0-10,16-26
146 | Time channel 4 start hour | 0-23
147 | Time channel 4 start minute | 0-59
148 | Time channel 4 stop hour | 0-23
149 | Time channel 4 stop minute | 0-59
150 | Time channel 5 status | 0-10,16-26
151 | Time channel 5 start hour | 0-23
152 | Time channel 5 start minute | 0-59
153 | Time channel 5 stop hour | 0-23
154 | Time channel 5 stop minute | 0-59
155 | Time channel 6 status | 0-10,16-26
156 | Time channel 6 start hour | 0-23
157 | Time channel 6 start minute | 0-59
158 | Time channel 6 stop hour | 0-23
159 | Time channel 6 stop minute | 0-59
160 | Time channel 7 status | 0-10,16-26
161 | Time channel 7 start hour | 0-23
162 | Time channel 7 start minute | 0-59
163 | Time channel 7 stop hour | 0-23
164 | Time channel 7 stop minute | 0-59
165 | Time channel 8 status | 0-10,16-26
166 | Time channel 8 start hour | 0-23
167 | Time channel 8 start minute | 0-59
168 | Time channel 8 stop hour | 0-23
169 | Time channel 8 stop minute | 0-59
170 | Extended low speed op. Hours | 0-23
Setting for extended low speed operation.
171 | Extended low speed op. Minutes | 0-59
Setting for extended low speed operation.
172 | Extended high speed op. Hours | 0-23
Setting for extended low speed operation.
173 | Extended high speed op. Minutes | 0-59
Setting for extended low speed operation.
174 | Communication operation mode | 0 - 4
Setting of unit operation mode from communication. 0=Auto operation (Normal stop when time channels are deactivated). 1=Communication stop 1. 2=Communication low speed. 3=Communication high speed. 4=Communication stop 2. Intermittent night heat and morning boost functions works at stop 2.
175 | Service periode alarm. | 0-99
Setting for delay time in months before service alarm.
176 | External alarm 1 delay | 1 - 600s
Setting of delay time for external alarm no 1
177 | External alarm 2 delay | 1 - 600s
Setting of delay time for external alarm no 2
178 | Int. Night heat SA pressure setpoint | 20-750Pa
Intermittent night heat function, supply pressure setpoint during night heat.
179 | Int. Night heat EA pressure setpoint | 20-750Pa
Intermittent night heat function, extract pressure setpoint during night heat.
180 | Copy of Coil Status 1-16 | 0-65535
Bit 0=1x0001 Bit 1=1x0002 Bit 15=1x0016
181 | Copy of Coil Statust 17-32 | 0-65535
Bit 0=1x00017 Bit 1=1x00018 Bit 15=1x0032
182 | Copy of Coil Status 33-48 | 0-65535
Bit 0=1x00033 Bit 1=1x00034 Bit 15=1x0048
183 | Heat relay periodic func. | 0-3
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
184 | Cool relay 1 periodic func. | 0-3
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
185 | Cool relay 2 periodic func. | 0-3
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
186 | Slave control C-factor | 0.5 - 2.0
Slave regulator affection setting.
187 | SA dehumid P-band | 1.00 - 40.00
SA dehumid regulator P-band setting.
188 | SA dehumid C-factor | 0.000 - 2.500
SA dehumid regulator affection setting.
189 | Dewpoint reg. P-band | 1.00 - 40.00
Dewpoint regulator P-band setting.
190 | Dewpoint reg. C-factor | 0.000 - 2.500
Dewpoint regulator affection setting.
191 | AYC chilled water temperature | 5.00-30.00°C
Setting of AYC chilled water temperature setpoint.
192 | Dewpoint neutralzone | 0.00-5.00°C
Dewpoint neutralzone setting.
193 | Comp. airflow | 0-30.00%
Setting of comp. airflow.
194 | Supply air-humidity | 10.00-90.00%
Setting of supply air-humidity.
195 | Water heating periodic op. time | 0-60min
Setting of periodic op. time (minute).
196 | Water heating interval | 0-168h
Setting of water heating interval time (hour).
197 | Cool periodic op. time | 0-60min
Setting of periodic op. time (minute).
198 | Cool interval | 0-168h
Setting of cool interval time (hour).
199 | Reserve
200 | EA/Room temperature (external) func. | 0-2
Setting of EA/Room temperature (external) function. 0= Inactive. 1= IQnomic. 2= Communication (4x0202).
201 | EA/Room temperature com. | -55.00-125.00°C
Setting of EA/Room temperature via communication.
202 | Outdoor temperature (external) func. | 0-2
Setting of outdoor temperature (external) function. 0= Inactive. 1= IQnomic. 2= Communication (4x0204).
203 | Outdoor temperature com. | -55.00-125.00°C
Setting of outdoor temperature via communication.
204 | Timeout temperature com. | 0-9999min
Setting of timeout for temperature via communication (4x0202, 4x0204).
205 | Flow at fire function. | 0-3
Setting for activating the air fan operation at fire function 0= Inactive. 1= SA. 2= EA. 3= SA+EA.
206 | Air fan down regulation func. | 0-2
Setting for activating the air fan down regulation function 0= Inactive. 1= SA. 2= SA+EA.
207 | SA speed at fire. | 10.00-100.00%
Setting of supply air speed at fire.
208 | EA speed at fire. | 10.00-100.00%
Setting of extract air speed at fire.
209 | Reserve
210 | Reserve
211 | Supply air min P-band. | 1.00 - 40.00
Supply air min regulator P-band setting.
212 | Supply air min C-factor. | 0.000 - 2.500
Supply air min regulator affection setting.
213 | Supply air max P-band. | 1.00 - 40.00
Supply air max regulator P-band setting.
214 | Supply air max C-factor. | 0.000 - 2.500
Supply air max regulator affection setting.
215 | Year channel 1 function. | 0 - 3
0 = Inactive. 1 = Stop. 2 = Low speed. 3 = High speed.
216 | Year channel 1 start year. | 2000 - 2099
217 | Year channel 1 start month. | 1 - 12
218 | Year channel 1 start date. | 1 - 31
219 | Year channel 1 start hour. | 0 - 23
220 | Year channel 1 start minute. | 0 - 59
221 | Year channel 1 stop year. | 2000 - 2099
222 | Year channel 1 stop month. | 1 - 12
223 | Year channel 1 stop date. | 1 - 31
224 | Year channel 1 stop hour. | 0 - 23
225 | Year channel 1 stop minute. | 0 - 59
226 | Year channel 2 function. | 0 - 3
227 | Year channel 2 start year. | 2000 - 2099
228 | Year channel 2 start month. | 1 - 12
229 | Year channel 2 start date. | 1 - 31
230 | Year channel 2 start hour. | 0 - 23
231 | Year channel 2 start minute. | 0 - 59
232 | Year channel 2 stop year. | 2000 - 2099
233 | Year channel 2 stop month. | 1 - 12
234 | Year channel 2 stop date. | 1 - 31
235 | Year channel 2 stop hour. | 0 - 23
236 | Year channel 2 stop minute. | 0 - 59
237 | Year channel 3 function. | 0 - 3
238 | Year channel 3 start year. | 2000 - 2099
239 | Year channel 3 start month. | 1 - 12
240 | Year channel 3 start date. | 1 - 31
241 | Year channel 3 start hour. | 0 - 23
242 | Year channel 3 start minute. | 0 - 59
243 | Year channel 3 stop year. | 2000 - 2099
244 | Year channel 3 stop month. | 1 - 12
245 | Year channel 3 stop date. | 1 - 31
246 | Year channel 3 stop hour. | 0 - 23
247 | Year channel 3 stop minute. | 0 - 59
248 | Year channel 4 function. | 0 - 3
249 | Year channel 4 start year. | 2000 - 2099
250 | Year channel 4 start month. | 1 - 12
251 | Year channel 4 start date. | 1 - 31
252 | Year channel 4 start hour. | 0 - 23
253 | Year channel 4 start minute. | 0 - 59
254 | Year channel 4 stop year. | 2000 - 2099
255 | Year channel 4 stop month. | 1 - 12
256 | Year channel 4 stop date. | 1 - 31
257 | Year channel 4 stop hour. | 0 - 23
258 | Year channel 4 stop minute. | 0 - 59
259 | Year channel 5 function. | 0 - 3
260 | Year channel 5 start year. | 2000 - 2099
261 | Year channel 5 start month. | 1 - 12
262 | Year channel 5 start date. | 1 - 31
263 | Year channel 5 start hour. | 0 - 23
264 | Year channel 5 start minute. | 0 - 59
265 | Year channel 5 stop year. | 2000 - 2099
266 | Year channel 5 stop month. | 1 - 12
267 | Year channel 5 stop date. | 1 - 31
268 | Year channel 5 stop hour. | 0 - 23
269 | Year channel 5 stop minute. | 0 - 59
270 | Year channel 6 function. | 0 - 3
271 | Year channel 6 start year. | 2000 - 2099
272 | Year channel 6 start month. | 1 - 12
273 | Year channel 6 start date. | 1 - 31
274 | Year channel 6 start hour. | 0 - 23
275 | Year channel 6 start minute. | 0 - 59
276 | Year channel 6 stop year. | 2000 - 2099
277 | Year channel 6 stop month. | 1 - 12
278 | Year channel 6 stop date. | 1 - 31
279 | Year channel 6 stop hour. | 0 - 23
280 | Year channel 6 stop minute. | 0 - 59
281 | Year channel 7 function. | 0 - 3
282 | Year channel 7 start year. | 2000 - 2099
283 | Year channel 7 start month. | 1 - 12
284 | Year channel 7 start date. | 1 - 31
285 | Year channel 7 start hour. | 0 - 23
286 | Year channel 7 start minute. | 0 - 59
287 | Year channel 7 stop year. | 2000 - 2099
288 | Year channel 7 stop month. | 1 - 12
289 | Year channel 7 stop date. | 1 - 31
290 | Year channel 7 stop hour. | 0 - 23
291 | Year channel 7 stop minute. | 0 - 59
292 | Year channel 8 function. | 0 - 3
293 | Year channel 8 start year. | 2000 - 2099
294 | Year channel 8 start month. | 1 - 12
295 | Year channel 8 start date. | 1 - 31
296 | Year channel 8 start hour. | 0 - 23
297 | Year channel 8 start minute. | 0 - 59
298 | Year channel 8 stop year. | 2000 - 2099
299 | Year channel 8 stop month. | 1 - 12
300 | Year channel 8 stop date. | 1 - 31
301 | Year channel 8 stop hour. | 0 - 23
302 | Year channel 8 stop minute. | 0 - 59
303 | Filter select. | 0 - 3
Setting for filter select function. 0=Inactive. 1=Supply air. 2=Extract air. 3=SA+EA.
304 | Prefilter select. | 0 - 3
Setting for prefilter select function. 0=Inactive. 1=Supply air. 2=Extract air. 3=SA+EA.
305 | SA prefilter alarm limit. | 10-1000Pa
Supply air prefilter pressure alarm limit setting.
306 | EA prefilter alarm limit. | 10-1000Pa
Extract air prefilter pressure alarm limit setting.
307 | Prefilter calibration mode. | 0 - 3
Setting for requiered filtercalibration. 0=Inactive. 1=SA+EA-Filter. 2=SA-Filter. 3=EA-Filter.
308 | Preheating function. | 0 - 4
Setting of preheating function. 0=Inactive. 1=El. coil P/P. 2=El. coil 0-10V. 3=Water coil with FP. 4=Water coil without FP.
309 | Preheating setpoint. | -30.00-30.00°C
Setting of preheating temperature setpoint.
310 | Preheat P-band. | 1.00 - 40.00
Preheat regulator P-band setting.
311 | Preheat C-factor. | 0.000 - 2.500
Preheat regulator affection setting.
312 | SA Filter calculated alarm level | 5.00-20.00%
Supply air filter calculated alarm limit setting.
313 | EA Filter calculated alarm level | 5.00-20.00%
Extract air filter calculated alarm limit setting.
314 | Mode digital output relay 1 | 0-8
Setting of mode output relay 1 function. 0=Damper. 1=Operation. 2=Low speed. 3=High speed. 4=Alarm A. 5=Alarm B. 6=Heating. 7=Cooling 1. 8=Cooling 2.
315 | Mode digital output relay 2 | 0-8
Setting of mode output relay 2 function. 0=Damper. 1=Operation. 2=Low speed. 3=High speed. 4=Alarm A. 5=Alarm B. 6=Heating. 7=Cooling 1. 8=Cooling 2.
316 | Mode digital input 1 | 0-6
Setting of mode input 1 function. 0=Stop. 1=Low speed. 2=High speed. 3=Alarm 1. 4=Alarm 2. 5=Reset. 6=Fire.
317 | Mode digital input 2 | 0-6
Setting of mode input 2 function. 0=Stop. 1=Low speed. 2=High speed. 3=Alarm 1. 4=Alarm 2. 5=Reset. 6=Fire.
318 | Manual morning boost time hour | 0-23
Setting of manual morning boost time before normal operation.
319 | Manual morning boost time minutes | 0-59
Setting of manual morning boost time before normal operation.
320 | Airing temp set | 10.00-20.00°C
Setting of airing temperature setpoint.
321 | Airing time set | 10-60
Setting of airing time in minutes.
322 | Manual operation drift mode | 0-4
Setting of manual operation drift mode. 0=Normal operation. 1=Extended operation. 2=Airing. 3=Heating. 4=Heating+Recirc.
323 | AYC function. | 0 - 3
Setting of AYC function. 0=Inactive. 1=Cool. 2=Heat. 3=Cool+heat.
324 | AYC heat temp set. | 10.00-80.00°C
Setting of AYC heated water temperature setpoint.
325 | AYC night comp. channel. | 1 - 2
Setting of AYC night compensation channel. 1=Channel 1. 2=Channel 2.
326 | AYC channel start hour. | 0-23h
Setting of AYC channel start time (hour).
327 | AYC channel start minute. | 0-59min
Setting of AYC channel start time (minute).
328 | AYC channel stop hour. | 0-23h
Setting of AYC channel stop time (hour).
329 | AYC channel stop minute. | 0-59min
Setting of AYC channel stop time (minute).
330 | AYC channel period. | 0-10
Setting of AYC channel period. 0=Inactive 1=Monday 2=Tuesday 3=Wednesday 4=Thursday 5=Friday 6=Saturday 7=Sunday 8=Monday..Friday 9=Monday..Sunday 10=Saturday..Sunday
331 | AYC heat P-band. | 1.00 - 40.00
AYC heat regulator P-band setting.
332 | AYC heat C-factor. | 0.000 - 2.500
AYC heat regulator affection setting.
333 | AYC cool P-band. | 1.00 - 40.00
AYC cool regulator P-band setting.
334 | AYC cool C-factor. | 0.000 - 2.500
AYC cool regulator affection setting.
335 | AYC heat out comp. X1. | -40.00-40.00°C
AYC outdoor compensation of heated water, outdoor temp X1 setting.
336 | AYC heat out comp. Y1. | 10.00-80.00°C
AYC outdoor compensation of heated water, heated water temp Y1 setting.
337 | AYC heat out comp. X2. | -40.00-40.00°C
AYC outdoor compensation of heated water, outdoor temp X2 setting.
338 | AYC heat out comp. Y2. | 10.00-80.00°C
AYC outdoor compensation of heated water, heated water temp Y2 setting.
339 | AYC heat out comp. X3. | -40.00-40.00°C
AYC outdoor compensation of heated water, outdoor temp X3 setting.
340 | AYC heat out comp. Y3. | 10.00-80.00°C
AYC outdoor compensation of heated water, heated water temp Y3 setting.
341 | AYC heat room comp. temp limit. | 0.00-40.00°C
AYC room compensation of heated water, heated water temp limit setting.
342 | AYC heat room comp P-band. | 1.00-10.00°C
AYC room compensation of heated water, heated water P-band setting.
343 | AYC heat night comp temp. | -10.00-10.00°C
AYC night compensation of heated water, heated water night setting.
344 | AYC heat pump on temp. | -40.00-40.00°C
AYC pump operation of heated water, outdoor temp start setting.
345 | AYC heat pump off temp. | -40.00-40.00°C
AYC pump operation of heated water, outdoor temp stop setting.
346 | AYC heat pump alarm. | 0 - 3
Setting for selecting the AYC heated water pump alarm function. 0=Inactive. 1=Open. 2=Closed. 3=Contactor.
347 | AYC heat per op function. | 0 - 3
Setting for selecting the AYC heated water periodic operation function. 0=Inactive. 1=Pump. 2=Pump+valve. 3=Valve.
348 | AYC heat per op time. | 0-60min
AYC periodic operation of heated water, time (minute) setting.
349 | AYC heat per op interval. | 0-168h
AYC periodic operation of heated water, interval time (hour) setting.
350 | AYC cool out comp. X1. | -40.00-40.00°C
AYC outdoor compensation of chilled water, outdoor temp X1 setting.
351 | AYC cool out comp. Y1. | 10.00-80.00°C
AYC outdoor compensation of chilled water, chilled water temp Y1 setting.
352 | AYC cool out comp. X2. | -40.00-40.00°C
AYC outdoor compensation of chilled water, outdoor temp X2 setting.
353 | AYC cool out comp. Y2. | 10.00-80.00°C
AYC outdoor compensation of chilled water, chilled water temp Y2 setting.
354 | AYC cool out comp. X3. | -40.00-40.00°C
AYC outdoor compensation of chilled water, outdoor temp X3 setting.
355 | AYC cool out comp. Y3. | 10.00-80.00°C
AYC outdoor compensation of chilled water, chilled water temp Y3 setting.
356 | AYC cool room comp. temp limit. | 0.00-40.00°C
AYC room compensation of chilled water, chilled water temp limit setting.
357 | AYC cool room comp. P-band. | 1.00-10.00°C
AYC room compensation of chilled water, chilled water P-band setting.
358 | AYC cool night comp temp. | -10.00-10.00°C
AYC night compensation of chilled water, chilled water night setting.
359 | AYC cool pump on temp. | -40.00-40.00°C
AYC pump operation of chilled water, outdoor temp start setting.
360 | AYC cool pump off temp. | -40.00-40.00°C
AYC pump operation of chilled water, outdoor temp stop setting.
361 | AYC cool pump alarm. | 0 - 3
Setting for selecting the AYC chilled water pump alarm function. 0=Inactive. 1=Open. 2=Closed. 3=Contactor.
362 | AYC cool per op function. | 0 - 3
Setting for selecting the AYC chilled water periodic operation function. 0=Inactive. 1=Pump. 2=Pump+valve. 3=Valve.
363 | AYC cool per op time. | 0-60min
AYC periodic operation of chilled water, time (minute) setting.
364 | AYC cool per op interval. | 0-168h
AYC periodic operation of chilled water, interval time (hour) setting.
365 | IO-mod 3 output 1 function. | 0 - 10
Setting of I/O-module no. 3 relay 1 output. 0=Cooling boost. 1=Heating boost. 2=Cooling. 3=Heat exchange. 4=Reheat. 5=Down regulation. 6=Effect reduction. 7=Intermittent night heat. 8=Summer night cooling. 9=Morning boost. 10=Heat exchange defrost.
366 | IO-mod 3 output 2 function. | 0 - 10
Setting of I/O-module no. 3 relay 2 output. 0=Cooling boost. 1=Heating boost. 2=Cooling. 3=Heat exchange. 4=Reheat. 5=Down regulation. 6=Effect reduction. 7=Intermittent night heat. 8=Summer night cooling. 9=Morning boost. 10=Heat exchange defrost.

## Binary Inputs
GB.BACnet480.100129
Binary Inputs (RO).
Object Instance | Object Name | Min/Max
0 | Heat output | 0-1
Status for relay output.
1 | Cool output 1 | 0-1
Status for relay output.
2 | Cool output 2 | 0-1
Status for relay output.
3 | Low speed output | 0-1
Status for relay output.
4 | High speed output | 0-1
Status for relay output.
5 | A-alarm. | 0-1
Status for relay output.
6 | B-alarm. | 0-1
Status for relay output.
7 | Operation output | 0-1
Status for relay output.
8 | Damper output | 0-1
Status for relay output.
9 | External low speed input | 0-1
Status for digital input.
10 | External high speed input | 0-1
Status for digital input.
11 | External alarm 1 input | 0-1
Status for digital input.
12 | External alarm 2 input | 0-1
Status for digital input.
13 | External fire alarm input. | 0-1
Status for digital input.
14 | External stop input | 0-1
Status for digital input.
15 | DIP Switch 1 | 0-1
Status for dip switch setting.
16 | DIP Switch 2 | 0-1
Status for dip switch setting.
17 | DIP Switch 3 | 0-1
Status for dip switch setting.
18 | DIP Switch 4 | 0-1
Status for dip switch setting.
19 | DIP Switch 5 | 0-1
Status for dip switch setting.
20 | DIP Switch 6 | 0-1
Status for dip switch setting.
21 | AYC heat pump output | 0-1
Status for AYC heat pump output.
22 | AYC cool pump output | 0-1
Status for AYC cool pump output.
23 | Reserve 9
24 | R.HX rotation monitor | 0-1
Status from the rotation detector.
25 | Reserve 10
26 | Reserve 11
27 | Reserve 12
28 | Pre-heat output | 0-1
Status for relay output.
29 | Recirculation output | 0-1
Status for I/O-module no. 3 relay 1 output.
30 | Booster output | 0-1
Status for I/O-module no. 3 relay 2 output.
31 | IO-mod 3 output 1 | 0-1
Status for I/O-module no. 3 relay 1 output.
32 | IO-mod 3 output 2 | 0-1
Status for I/O-module no. 3 relay 2 output.
33 | Reserve 13
34 | Reserve 14
35 | Reserve 15
36 | Reserve 16
37 | Reserve 17
38 | Reserve 18
39 | Reserve 19
40 | Reserve 20
41 | Reserve 21
42 | Reserve 22
43 | Reserve 23
44 | Reserve 24
45 | Reserve 25
46 | Reserve 26
47 | Reserve 27
48 | Alarm number 1 | 0-1
Status if alarm number 1 is active.
49 | Alarm number 2 | 0-1
Status if alarm number 2 is active.
50 | Alarm number 3 | 0-1
Status if alarm number 3 is active.
247 | Alarm number 200 | 0-1
Status if alarm number 200 is active.
248 | Info number 1 | 0-1
Status if info number 1 is active.
249 | Info number 2 | 0-1
Status if info number 2 is active.
250 | Info number 3 | 0-1
Status if info number 3 is active.
347 | Info number 100 | 0-1
Status if info number 100 is active.

## Binary Value
GB.BACnet480.100129
Binary Value (R/W).
Object Instance | Object Name | Min/Max
0 | Alarm reset | 0-1
Resets tripped alarms.
1 | R.HX. Defrost func. | 0-1
Setting for activating the defrost function for the rotary heat exchanger.
2 | Cool operation mode | 0-1
Setting for cooling between off and auto operation.
3 | Int. Night heat func. | 0-1
Setting for activating the intermittent night heat function.
4 | Damper func. | 0-1
Setting for activating the damper output relay during int. night heat.
5 | Summer night cooling | 0-1
Setting for activating the suumer night cool function.
6 | Outdoor temp compensation | 0-1
Setting for activating the outdoor temperature compensation function.
7 | Outdoor airflow compensation | 0-1
Setting for activating the outdoor airflow compensation function.
8 | Auto. Summer/winter switch | 0-1
Setting for activating the automatic switch between summer/winter time function.
9 | Switch clock func. | 0-1
Setting for switch clock function type. 0=Stop - low speed - high speed. 1=Low speed - high speed.
10 | Internal fire alarm func. | 0-1
Setting for activating the internal fire alarm function.
11 | External alarm 1 active at closure | 0-1
Setting for external alarm number 1 condition to be activated. 0=Alarm at closed input. 1=Alarm at open input.
12 | External alarm 2 active at closure | 0-1
Setting for external alarm number 2 condition to be activated. 0=Alarm at closed input. 1=Alarm at open input.
13 | Dewpoint reg. func. | 0-1
Setting for activating the dewpoint regulator funktion.
14 | Dehumid reg. func. | 0-1
Setting for activating the dehumid regulator funktion.
15 | External fire alarm func. | 0-1
Setting for external fire resetting function. 0=Manual. 1=Automatic.
16 | External alarm 1 func. | 0-1
Setting for external alarm 1 resetting function. 0=Manual. 1=Automatic.
17 | External alarm 2 func. | 0-1
Setting for external alarm 2 resetting function. 0=Manual. 1=Automatic.
18 | Int. Night heat output func. | 0-1
Setting for selecting the intermittent night heat output function. 0=IQnomic 1=IQnomic+
19 | Morningboost damper func. | 0-1
Setting for activating the morningboost damper function. 0= Inactive. 1= Active.
20 | Morningboost extract func. | 0-1
Setting for activating the morningboost extract air fan function. 0= Inactive. 1= Active.
21 | Filter func. | 0-1
Setting for filter between calculated and pressure sensors. 0=Calculated. 1=Pressure sensors.
22 | Iqnomic Plus module no.6 Cooling | 0-1
Setting for activating Iqnomiq Plus no.6 Cooling module. 0=Inactive. 1=Active.
23 | Airing auto func. | 0-1
Setting for activating the airing auto function. 0=Inactive. 1=Active.
24 | AYC heat out comp. func. | 0-1
Setting for selecting the AYC outdoor comp. heated water function. 0=Inactive 1=Active
25 | AYC heat room comp. func. | 0-1
Setting for selecting the AYC room comp. heated water function. 0=Inactive 1=Active
26 | AYC heat room comp. night block func. | 0-1
Setting for selecting the AYC room comp. heated water night block function. 0=Inactive 1=Active
27 | AYC heat night comp. func. | 0-1
Setting for selecting the AYC night comp. heated water function. 0=Inactive 1=Active
28 | AYC heat valve signal func. | 0-1
Setting for selecting the AYC valve signal heated water alarm function. 0=Inactive 1=Active
29 | AYC cool out comp. func. | 0-1
Setting for selecting the AYC outdoor comp. chilled water function. 0=Inactive 1=Active
30 | AYC cool room comp. func. | 0-1
Setting for selecting the AYC room comp. chilled water function. 0=Inactive 1=Active
31 | AYC cool room comp. night block func. | 0-1
Setting for selecting the AYC room comp. chilled water night block function. 0=Inactive 1=Active
32 | AYC cool night comp. func. | 0-1
Setting for selecting the AYC night comp. chilled water function. 0=Inactive 1=Active
33 | AYC cool valve signal func. | 0-1
Setting for selecting the AYC valve signal chilled water alarm function. 0=Inactive 1=Active