## Overview_data
GB.ModBus480.120417
Modbus RTU/TCP
GOLD RX/PX/CX/SD, GENERATION C/D
Applicable to program version 1.05 and newer versions
Overview
ModBus can access single addresses or multiple addresses
simultaneously; either reading or writing single bit values
or 16-bit values.
A ModBus address contains either a 1-bit discrete value or
a 16-bit integer value.
ModBus data format
ModBus data types are 1-bit values and 16-bit values.
ModBus Type |  | Description | Reference
Coli Status |  | Discrete Output | 0x
Input Status |  | Discrete Input | 1x
Holding Register |  | 16-bit Output Register | 4x
Input Register |  | 16-bit Input Register | 3x
Supported ModBus commands
The GOLD air handling unit supports these ModBus commands.
Function code | Description
01 | Read Coil Status
02 | Read Input Status
03 | Read Holding Registers
04 | Read Input Registers
05 | Force Single Coil
06 | Present Single Registers
08 | Diagnostics.Sub-funktion 00 Only - Return Query Data (loop back).
15 | Force Multiple Colis
16 | Present Multiple Registers

## Overview parameters
GB.ModBus480.120417
Operation mode 1 |  | 3x0085 |  | Extract air filter pressure level |  | 3x0053 |  | EA/Room temperature |  | 3x0029
Communication operation mode |  | 4x0175 |  | EA filter pressure level limit |  | 3x0054 |  | EA/Room temperature setpoint |  | 4x0042
Operation mode 2 |  | 3x0086 | [5 empty] | SA Min temperature setpoint |  | 4x0043
Operation output |  | 1x0008 | [5 empty] | SA Max temperature setpoint |  | 4x0044
Low speed output |  | 1x0004 |  |  | EA Duct pressure |  | 3x0007
High speed output |  | 1x0005 |  |  | EA Low speed pressure setpoint |  | 4x0013
Damper output |  | 1x0009 |  |  | EA High speed pressure setpoint |  | 4x0014 | SA Duct Pressure |  | 3x0005
Present tripped alarm |  | 3x0079 | [5 empty] | SA Low speed pressure setpoint |  | 4x0009
A-alarm |  | 1x0006 | [5 empty] | SA High speed pressure setpoint |  | 4x0010
B-alarm |  | 1x0007
Alarm reset |  | 0x0001
[8 empty] | SA Temperature |  | 3x0028
[8 empty] | SA Temperature setpoint |  | 4x0041
EA Airflow |  | 3x0003 | [5 empty] | ERS 1 Diff |  | 4x0033
EA Fan level |  | 3x0014
EA Low speed airflow setpoint |  | 4x0005
EA High speed airflow setpoint |  | 4x0006
Outdoor temperature |  | 3x0030
Supply air filter pressure level |  | 3x0050
SA filter pressure level limit |  | 3x0051
Heat exchange regulator |  | 3x0091
| SA Airflow |  | 3x0001 |  | Reheat level |  | 3x0037 | Cooling level |  | 3x0040
| SA Fan level |  | 3x0013 |  | Heat output |  | 1x0001 | Cool output 1 |  | 1x0002
| SA Low speed airflow setpoint |  | 4x0001 |  | Anti frost temperature |  | 3x0033 | Cool output 2 |  | 1x0003
| SA High speed airflow setpoint |  | 4x0002

## Coil Status
GB.ModBus480.120417
Coil Status. 1bit (R/W).
Modbus | Name | Min/Max | Misc
0x0001 | Alarm reset | 0-1
Resets tripped alarms.
0x0002 | SA Boosting func. | 0-1
Setting for activating the boost function for the supply air fan.
0x0003 | EA Boosting func. | 0-1
Setting for activating the boost function for the extract air fan.
0x0004 | R.HX. Defrost func. | 0-1
Setting for activating the defrost function for the rotary heat exchanger.
0x0005 | SA Down regulation func. | 0-1 | PV 3.00
Setting for activating the down regulation function for the supply air fan. (Moved to 4x0207 in PV 3.00)
0x0006 | Reserve
0x0007 | Reserve
0x0008 | Cool operation mode | 0-1
Setting for cooling between off and auto operation.
0x0009 | Int. Night heat func. | 0-1
Setting for activating the intermittent night heat function.
0x0010 | Damper func. | 0-1
Setting for activating the damper output relay during int. night heat.
0x0011 | Summer night cooling | 0-1
Setting for activating the summer night cool function.
0x0012 | Temp displacement | 0-1
Setting for activating the external temperature displacement function.
0x0013 | Outdoor temp compensation | 0-1
Setting for activating the outdoor temperature compensation function.
0x0014 | Outdoor airflow compensation | 0-1
Setting for activating the outdoor airflow compensation function.
0x0015 | Auto. Summer/winter switch | 0-1
Setting for activating the automatic switch between summer/winter time function.
0x0016 | Switch clock func. | 0-1
Setting for switch clock function type. 0=Stop - low speed - high speed. 1=Low speed - high speed.
0x0017 | Internal fire alarm func. | 0-1
Setting for activating the internal fire alarm function.
0x0018 | EA at fire | 0-1 | PV 3.00
Setting for activating the extract air fan operation at fire function. (Moved to 4x0206 in PV 3.00)
0x0019 | External alarm 1 active at closure | 0-1
Setting for external alarm number 1 condition to be activated. 0=Alarm at closed input. 1=Alarm at open input.
0x0020 | External alarm 2 active at closure | 0-1
Setting for external alarm number 2 condition to be activated. 0=Alarm at closed input. 1=Alarm at open input.
0x0021 | Reserve
0x0022 | Dewpoint reg. func. | 0-1
Setting for activating the dewpoint regulator function.
0x0023 | Dehumid reg. func. | 0-1
Setting for activating the dehumidify regulator function.
0x0024 | External fire alarm func. | 0-1 | PV 3.00
Setting for external fire resetting function. 0=Manual. 1=Automatic.
0x0025 | External alarm 1 func. | 0-1 | PV 3.00
Setting for external alarm 1 resetting function. 0=Manual. 1=Automatic.
0x0026 | External alarm 2 func. | 0-1 | PV 3.00
Setting for external alarm 2 resetting function. 0=Manual. 1=Automatic.
0x0027 | Temperature alarm func. | 0-1 | PV 3.00
Setting for activating temperature below setpoint alarm function (no.80).
0x0028 | Int. Night heat output func. | 0-1 | PV 5.00
Setting for selecting the intermittent night heat output function. 0=IQnomic 1=IQnomic+
0x0029 | AYC heat out comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC outdoor comp. heated water function. 0=Inactive 1=Active
0x0030 | AYC heat room comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC room comp. heated water function. 0=Inactive 1=Active
0x0031 | AYC heat room comp. night block func. | 0-1 | PV 5.07
Setting for selecting the AYC room comp. heated water night block function. 0=Inactive 1=Active
0x0032 | AYC heat night comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC night comp. heated water function. 0=Inactive 1=Active
0x0033 | AYC heat valve signal func. | 0-1 | PV 5.07
Setting for selecting the AYC valve signal heated water alarm function. 0=Inactive 1=Active
0x0034 | AYC cool out comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC outdoor comp. chilled water function. 0=Inactive 1=Active
0x0035 | AYC cool room comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC room comp. chilled water function. 0=Inactive 1=Active
0x0036 | AYC cool room comp. night block func. | 0-1 | PV 5.07
Setting for selecting the AYC room comp. chilled water night block function. 0=Inactive 1=Active
0x0037 | AYC cool night comp. func. | 0-1 | PV 5.07
Setting for selecting the AYC night comp. chilled water function. 0=Inactive 1=Active
0x0038 | AYC cool valve signal func. | 0-1 | PV 5.07
Setting for selecting the AYC valve signal chilled water alarm function. 0=Inactive 1=Active
0x0039 | BB func. | 0-1 | PV 6.05
Setting for selecting the Blue Box function. 0=Inactive 1=Active
0x0040 | BB optimize temp. func. | 0-1 | PV 6.05
Setting for selecting the Blue Box optimize temperature function. 0=Inactive 1=Active
0x0041 | Season heat mode | 0-1 | PV 6.07
Setting for selecting season heating mode. 0=Inactive 1=Active
0x0042 | Steam humid alarm input | 0-1 | PV 6.07
Setting for selecting steam humidification alarm input. 0=NO(Alarm at open input) 1=NC(Alarm at closed input)
0x0043 | ReCO2 zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of ReCO2 pressure sensor. 0=Inactive 1=Active
0x0044 | EA flow zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of extract air flow pressure sensor. 0=Inactive 1=Active
0x0045 | SA flow zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of supply air flow pressure sensor. 0=Inactive 1=Active
0x0046 | SA filt zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of supply air filter pressure sensor. 0=Inactive 1=Active
0x0047 | EA filt zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of extract air filter pressure sensor. 0=Inactive 1=Active
0x0048 | SA duct zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of supply air duct pressure sensor. 0=Inactive 1=Active
0x0049 | EA duct zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of extract air duct pressure sensor. 0=Inactive 1=Active
0x0050 | R.HX zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of rotary heat exchanger pressure sensor. 0=Inactive 1=Active
0x0051 | SA pre-filt zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of supply air pre-filter pressure sensor. 0=Inactive 1=Active
0x0052 | EA pre-filt zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of extract air pre-filter pressure sensor. 0=Inactive 1=Active
0x0053 | SA end-filt zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of supply air end-filter pressure sensor. 0=Inactive 1=Active
0x0054 | NU B zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of not used position B pressure sensor. 0=Inactive 1=Active
0x0055 | NU C zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of not used position C pressure sensor. 0=Inactive 1=Active
0x0056 | NU D zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of not used position D pressure sensor. 0=Inactive 1=Active
0x0057 | NU E zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of not used position E pressure sensor. 0=Inactive 1=Active
0x0058 | NU F zero cal. | 0-1 | PV 6.07
Setting for selecting zero calibration of not used position F pressure sensor. 0=Inactive 1=Active
0x0059 | ReCO2 man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of ReCO2 pressure sensor. 0=Auto 1=Manual
0x0060 | EA flow man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of extract air flow pressure sensor. 0=Auto 1=Manual
0x0061 | SA flow man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of supply air flow pressure sensor. 0=Auto 1=Manual
0x0062 | SA filt man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of supply air filter pressure sensor. 0=Auto 1=Manual
0x0063 | EA filt man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of extract air filter pressure sensor. 0=Auto 1=Manual
0x0064 | SA duct man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of supply air duct pressure sensor. 0=Auto 1=Manual
0x0065 | EA duct man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of extract air duct pressure sensor. 0=Auto 1=Manual
0x0066 | R.HX man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of rotary heat exchanger pressure sensor. 0=Auto 1=Manual
0x0067 | SA pre-filt man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of supply air pre-filter pressure sensor. 0=Auto 1=Manual
0x0068 | EA pre-filt man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of extract air pre-filter pressure sensor. 0=Auto 1=Manual
0x0069 | SA end-filt man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of supply air end-filter pressure sensor. 0=Auto 1=Manual
0x0070 | NU B man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of not used position B pressure sensor. 0=Auto 1=Manual
0x0071 | NU C man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of not used position C pressure sensor. 0=Auto 1=Manual
0x0072 | NU D man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of not used position D pressure sensor. 0=Auto 1=Manual
0x0073 | NU E man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of not used position E pressure sensor. 0=Auto 1=Manual
0x0074 | NU F man mode zero cal. | 0-1 | PV 6.07
Setting for selecting manual mode of zero calibration of not used position F pressure sensor. 0=Auto 1=Manual

## Input Status
GB.ModBus480.120417
Input Status. 1bit (RO).
Modbus | Name | Min/Max | Misc
1x0001 | Heat output | 0-1
Status for relay output.
1x0002 | Cool output 1 | 0-1
Status for relay output.
1x0003 | Cool output 2 | 0-1
Status for relay output.
1x0004 | Low speed output | 0-1
Status for relay output.
1x0005 | High speed output | 0-1
Status for relay output.
1x0006 | A-alarm. | 0-1
Status for relay output.
1x0007 | B-alarm. | 0-1
Status for relay output.
1x0008 | Operation output | 0-1
Status for relay output.
1x0009 | Damper output | 0-1
Status for relay output.
1x0010 | External low speed input | 0-1
Status for digital input.
1x0011 | External high speed input | 0-1
Status for digital input.
1x0012 | External alarm 1 input | 0-1
Status for digital input.
1x0013 | External alarm 2 input | 0-1
Status for digital input.
1x0014 | External fire alarm input. | 0-1
Status for digital input.
1x0015 | External stop input | 0-1
Status for digital input.
1x0016 | DIP Switch 1 | 0-1
Status for dip switch setting.
1x0017 | DIP Switch 2 | 0-1
Status for dip switch setting.
1x0018 | DIP Switch 3 | 0-1
Status for dip switch setting.
1x0019 | DIP Switch 4 | 0-1
Status for dip switch setting.
1x0020 | DIP Switch 5 | 0-1
Status for dip switch setting.
1x0021 | DIP Switch 6 | 0-1
Status for dip switch setting.
1x0022 | AYC heat pump output | 0-1 | PV 5.07
Status for AYC heat pump output.
1x0023 | AYC cool pump output | 0-1 | PV 5.07
Status for AYC cool pump output.
1x0024 | C.HX. pump output | 0-1 | PV 2.00
Status for coil heat exchanger pump output.
1x0025 | R.HX rotation monitor | 0-1 | PV 3.00
Status from the rotation detector.
1x0026 | Xzone heat output | 0-1 | PV 5.00
Status for relay output.
1x0027 | Xzone cool output 1 | 0-1 | PV 5.00
Status for relay output.
1x0028 | Xzone cool output 2 | 0-1 | PV 5.00
Status for relay output.
1x0029 | Pre-heat output | 0-1 | PV 5.00
Status for relay output.
1x0030 | IO-mod 3 output 1 | 0-1 | PV 5.07
Status for I/O-module no. 3 relay 1 output.
1x0031 | IO-mod 3 output 2 | 0-1 | PV 5.07
Status for I/O-module no. 3 relay 2 output.
1x0032 | IO-mod 4 output 1 | 0-1 | PV 5.10
Status for I/O-module no. 4 relay 1 output.
1x0033 | Miru 1 Alarm | 0-1 | PV 6.04
Status of group alarm from Miru fan.
1x0034 | Miru 2 Alarm | 0-1 | PV 6.04
Status of group alarm from Miru fan.
1x0035 | Miru 3 Alarm | 0-1 | PV 6.04
Status of group alarm from Miru fan.
1x0036 | Miru 4 Alarm | 0-1 | PV 6.04
Status of group alarm from Miru fan.
1x0037 | Miru 5 Alarm | 0-1 | PV 6.04
Status of group alarm from Miru fan.
1x0038 | Miru 6 Alarm | 0-1 | PV 6.04
Status of group alarm from Miru fan.
1x0039 | Miru 7 Alarm | 0-1 | PV 6.04
Status of group alarm from Miru fan.
1x0040 | Miru 8 Alarm | 0-1 | PV 6.04
Status of group alarm from Miru fan.
1x0041 | Miru 9 Alarm | 0-1 | PV 6.04
Status of group alarm from Miru fan.
1x0042 | Miru 10 Alarm | 0-1 | PV 6.04
Status of group alarm from Miru fan.
1x0043 | Extended ext. reg. seq. Pump | 0-1 | PV 6.07
Status of extended extra regulation sequence pump output.
1x0044 | Season heating mode | 0-1 | PV 6.07
Status of season heating mode.
1x0045 | Reserve 24
1x0046 | Reserve 25
1x0047 | Reserve 26
1x0048 | Reserve 27
1x0049 | Alarm number 1 | 0-1
Status if alarm number 1 is active.
1x0050 | Alarm number 2 | 0-1
Status if alarm number 2 is active.
1x0051 | Alarm number 3 | 0-1
Status if alarm number 3 is active.
1x0248 | Alarm number 200 | 0-1 | PV 5.00
Status if alarm number 200 is active.
1x0249 | Info number 1 | 0-1 | PV 5.00
Status if info number 1 is active.
1x0250 | Info number 2 | 0-1 | PV 5.00
Status if info number 2 is active.
1x0251 | Info number 3 | 0-1 | PV 5.00
Status if info number 3 is active.
1x0348 | Info number 100 | 0-1 | PV 5.00
Status if info number 100 is active.

## Input Registers
GB.ModBus480.120417
Input Registers. 16-bit integer value (RO).
Modbus | Name | Min/Max | Misc
3x0001 | SA Airflow | 0-20000l/s
Present supply airflow.
3x0002 | SA Airflow regulator | 0-20000l/s
Present supply airflow regulator setpoint.
3x0003 | EA Airflow | 0-20000l/s
Present extract airflow.
3x0004 | EA Airflow regulator | 0-20000l/s
Present extract airflow regulator setpoint.
3x0005 | SA Duct pressure | 0-2000Pa
Present supply air duct pressure.
3x0006 | SA Duct pressure regulator | 0-2000Pa
Present supply air duct pressure regulator setpoint.
3x0007 | EA Duct pressure | 0-2000Pa
Present extract air duct pressure.
3x0008 | EA Duct pressure regulator | 0-2000Pa
Present extract air duct pressure regulator setpoint.
3x0009 | SA VAV demand/boost input | 0-100.00%
Present input signal for supply air VAV demand or boosting function.
3x0010 | SA VAV demand regulator | 0-100.00%
Present supply air VAV demand regulator setpoint.
3x0011 | EA VAV demand/boost input | 0-100.00%
Present input signal for extract air VAV demand or boosting function.
3x0012 | EA VAV demand regulator | 0-100.00%
Present supply air VAV demand regulator setpoint.
3x0013 | SA Fan level | 0-100.00%
Present running level for the supply air fan.
3x0014 | EA Fan level | 0-100.00%
Present running level for the extract air fan.
3x0015 | SA Fan power | 0-32700W | PV 6.04
Present power consumption level for the supply air fan. Also included slaves. PV 6.04
3x0016 | EA Fan power | 0-32700W | PV 6.04
Present power consumption level for the extract air fan. Also included slaves. PV 6.04
3x0017 | SFP | 0.0-9.9
SFP supply air + extract air.
3x0018 | SA Frequency | 0-100.00Hz
Present frequency level for the supply air fan.
3x0019 | EA Frequency | 0-100.00Hz
Present frequency level for the extract air fan.
3x0020 | SA Voltage | 0-500V
Present voltage level for the supply air fan.
3x0021 | EA Voltage | 0-500V
Present voltage level for the extract air fan.
3x0022 | SA Current | 0-32.700A | PV 6.04
Present current level for the supply air fan. Also included slaves. PV 6.04
3x0023 | EA Current | 0-32.700A | PV 6.04
Present current level for the extract air fan. Also included slaves. PV 6.04
3x0024 | SA Airflow pressure | 0-2000Pa
Present airflow pressure in the supply air fan inlet.
3x0025 | EA Airflow pressure | 0-2000Pa
Present airflow pressure in the extract air fan inlet.
3x0026 | SA Temp regulator | -55.00-125.00°C
Present supply air temperature regulator setpoint.
3x0027 | EA Temp regulator | -55.00-125.00°C
Present extract air temperature regulator setpoint.
3x0028 | SA Temperature | -55.00-125.00°C
Present supply air temperature.
3x0029 | EA/Room temperature | -55.00-125.00°C
Present extract air/room temperature in the unit.
3x0030 | Outdoor temperature | -55.00-125.00°C
Present outdoor air temperature in the unit.
3x0031 | EA/Room temperature (external) | -55.00-125.00°C
Present room temperature external from the unit.
3x0032 | Outdoor temperature (external) | -55.00-125.00°C
Present outdoor air temperature external from the unit.
3x0033 | Anti frost temperature | -55.00-125.00°C
Present anti frost temperature for water reheating coils.
3x0034 | Temperature sensor 3 | -55.00-125.00°C
Present temperature for temp sensor no.3
3x0035 | Temperature sensor 4 | -55.00-125.00°C
Present temperature for temp sensor no.4
3x0036 | Rotary heat exchanger level | 0-100.00%
Present operation level from rotary heat exchanger.
3x0037 | Reheat level | 0-100.00%
Present level of reheat.
3x0038 | SA Down regulation level | 0-100.00%
Present level of supply airflow down regulation.
3x0039 | Extra regulation sequence level | 0-100.00%
Present level of the extra regulation sequence.
3x0040 | Cooling level | 0-100.00%
Present level of cooling.
3x0041 | Heating boost level | 0-100.00%
Present level of heating boost.
3x0042 | Cooling boost level | 0-100.00%
Present level of cooling boost.
3x0043 | HX pressure level | 0-2000Pa
Present pressure drop for the rotary heat exchanger.
3x0044 | HX pressure alarm limit | 0-2000Pa
Present pressure drop alarm limit for the rotary heat exchanger.
3x0045 | HX temperature | 0-100.00°C
Present temperature inside the control unit for the rotary heat exchanger.
3x0046 | Effect reduction level | 0-100.00%
Present level of max output signal for electrical reheaters, active during low supply airflow.
3x0047 | Anti frost temp setpoint/operation | 10.00-16.00°C
Present anti frost temperature setpoint for water reheating coils during unit operation.
3x0048 | Anti frost temp setpoint/stop | 15.00-40.00°C
Present anti frost temperature setpoint for water reheating coils when the unit is in stop.
3x0049 | Anti frost temp alarm limit | 5.00-30.00°C
Setting of antifrost temperature alarm limit.
3x0050 | Supply air filter pressure level | 0-2000Pa
Present supply air filter pressure drop.
3x0051 | Supply air filter pressure alarm limit. | 0-2000Pa
Present supply air filter pressure alarm limit.
3x0052 | Supply air filter pressure level, new | 0-2000Pa
Supply air filter pressure saved from calibration.
3x0053 | Extract air filter pressure level | 0-2000Pa
Present extract air filter pressure drop.
3x0054 | Extract air filter pressure alarm limit. | 0-2000Pa
Present extract air filter pressure alarm limit.
3x0055 | Extract air filter pressure level, new | 0-2000Pa
Extract air filter pressure saved from calibration.
3x0056 | Temperature displacement | -5.00 - 5.00°C
Present temperature displacement from input signal.
3x0057 | Coil type | 0-20
Present connected reheat coil type.
3x0058 | Cool step time | 0-600s
Present time between cool step shift.
3x0059 | Cool relay 1 restart time | 0-900s
Present time between two starts of cool relay 1.
3x0060 | Cool relay 2 restart time | 0-900s
Present time between two starts of cool relay 2.
3x0061 | Program version, HMI | 0-10.00
Present program version for the hand held terminal.
3x0062 | Program version, HMI-slave | 0-10.00
Present program version for the extra hand held terminal.
3x0063 | Program version, main controller. | 0-10.00
Present program version for the main control unit.
3x0064 | Program version, SA FC-1. | 0-10.00
Present program version for the supply air frequency converter no.1.
3x0065 | Program version, SA FC-2. | 0-10.00
Present program version for the supply air frequency converter no.2.
3x0066 | Program version, EA FC-1. | 0-10.00
Present program version for the extract air frequency converter no.1.
3x0067 | Program version, EA FC-2. | 0-10.00
Present program version for the extract air frequency converter no.2.
3x0068 | Program version, HX control unit | 0-10.00
Present program version for the rotary heat exchange control unit.
3x0069 | Weekday | 0 - 6
Present weekday for the unit's internal clock.
3x0070 | Extended low speed op. Hours | 0-23
Present time for extended low speed operation.
3x0071 | Extended low speed op. Minutes | 0-59
Present time for extended low speed operation.
3x0072 | Extended high speed op. Hours | 0-23
Present time for extended high speed operation.
3x0073 | Extended high speed op. Minutes | 0-59
Present time for extended high speed operation.
3x0074 | SA Fan operation time | 0-9999
Present operation time for the supply air fan, measured in minutes and present in days (24h).
3x0075 | EA Fan operation time | 0-9999
Present operation time for the extract air fan, measured in minutes and present in days (24h).
3x0076 | Cool operation time | 0-9999
Present operation time for cooling, measured in minutes and present in days (24h).
3x0077 | Heat exchange operation time | 0-9999
Present operation time for heat exchange, measured in minutes and present in days (24h).
3x0078 | Reheat operation time | 0-9999
Present operation time for reheat, measured in minutes and present in days (24h).
3x0079 | Present tripped alarm | 0-200 | PV 5.00
Present tripped alarm number with highest priority.
3x0080 | Active not tripped alarm no.1 | 0-200 | PV 5.00
Present active alarm in delay.
3x0081 | Active not tripped alarm no.2 | 0-200 | PV 5.00
Present active alarm in delay.
3x0082 | Active not tripped alarm no.3 | 0-200 | PV 5.00
Present active alarm in delay.
3x0083 | SA Fan size | 04 - 120
Present supply air fan size.
3x0084 | EA Fan size | 04 - 120
Present extract air fan size.
3x0085 | Operation mode 1 | 0 - 18 | PV 5.00
0=Manual stop. 1=Ext. stop. 2=Com. stop 1. 3=Manual high speed. 4=Summer night cooling. 5=Int. night heat. 6=Manual low speed. 7=Ext. high speed. 8=Com. high speed. 9=Year channel stop. 10=Year channel high speed. 11=Year channel low speed. 12=Time channel high speed. 13=Ext. low speed. 14=Com. low speed. 15=Time channel low speed. 16=Time channel stop. 17=Low speed=stop. 18=Com. stop 2. (New in PV 5.00)
3x0086 | Operation mode 2 | 0 - 22 | PV 5.00
0= 1=Cold air recovery. 2=Cooling boost. 3=SA down regulation. 4=HX defrosting. 5=Anti frost func. active. 6=Effect reduction. 7=Startup. 8=Zero calibration. 9=Extended low speed. 10=Extended high speed. 11=Air adjustment. 12=Cooling off. 13=Purging R.HX. 14=Extended R.HX. op. 15=Filter calibration. 16=R.HX. calibration 17=Morning boost. 18=Heating boost. 19=Alarm. 20=CoolDX pressure reduction. (PV 2.00) 21=Startup extract air fan (New in 4.00) R.HX speed limited. (Only in PV 2.00-2.02) 22=Fan heat retention (New in PV 5.00)
3x0087 | Operation mode, manual | 0 - 3
Present manual operation set on the unit's hand held terminal. 0=Stop. 1=Auto operation. 2=Manual low speed. 3=Manual high speed.
3x0088 | Copy of Input Status 1-16. | 0-65535
Bit 0=1x0001 Bit 1=1x0002 Bit 15=1x0016
3x0089 | Copy of Input Status 17-32. | 0-65535
Bit 0=1x00017 Bit 1=1x00018 Bit 15=1x0032
3x0090 | Copy of Input Status 33-48. | 0-65535
Bit 0=1x00033 Bit 1=1x00034 Bit 15=1x0048
3x0091 | Heat exchanger regulator | 0-100.00%
Present level of heat exchanger regulator RX/CX/PX.
3x0092 | Extract air-humidity | 0-100.00%
Present level of extract air-humidity.
3x0093 | Extract air-humidity temperature | -55.00-125.00°C
Present temperature inside extract air-humidity sensor.
3x0094 | Extract air-dewpoint | -55.00-125.00°C
Calculated extract air-dewpoint.
3x0095 | AYC chilled water temperature | -55.00-125.00°C
Present AYC chilled water temperature.
3x0096 | AYC chilled water temperature regulator | -55.00-125.00°C
Present AYC chilled water temperature regulator setpoint.
3x0097 | AYC chilled water output | 0-100.00%
Present level of AYC chilled water valve output.
3x0098 | Supply air-dewpoint regulator | -55.00-125.00°C
Present supply air-dewpoint regulator setpoint.
3x0099 | Supply air-humidity | 0-100.00%
Present level of supply air-humidity
3x0100 | Supply air-humidity temperature | -55.00-125.00°C
Present temperature inside supply air-humidity sensor.
3x0101 | Supply air-dewpoint | -55.00-125.00°C
Calculated supply air-dewpoint.
3x0102 | C.HX. Temperature | -55.00-125.00°C | PV 2.00
Present temperature of coil heat exchanger.
3x0103 | P.HX. Temperature 1 | -55.00-125.00°C | PV 2.00
Present temperature 1 of plate heat exchanger.
3x0104 | P.HX. Temperature 2 | -55.00-125.00°C | PV 2.00
Present temperature 2 of plate heat exchanger.
3x0105 | P/C.HX. Humidity | 0-100.00% | PV 2.00
Present level of air-humidity in plate/coil heat exchanger.
3x0106 | R.HX. Efficiency | 0-100.00% | PV 2.00
Calculated level of rotary heat exchanger efficiency.
3x0107 | C.HX. Valve output | 0-100.00% | PV 5.00
Present level of coil heat exchanger valve output.
3x0108 | P.HX bypass output | 0-100.00% | PV 5.00
Present level of plate heat exchanger bypass output.
3x0109 | Supply air pre-filter pressure level | 0-2000Pa | PV 5.00
Present supply air pre-filter pressure drop.
3x0110 | Supply air pre-filter pressure alarm limit. | 0-2000Pa | PV 5.00
Present supply air pre-filter pressure alarm limit.
3x0111 | Supply air pre-filter pressure level, new | 0-2000Pa | PV 5.00
Supply air pre-filter pressure saved from calibration.
3x0112 | Extract air pre-filter pressure level | 0-2000Pa | PV 5.00
Present extract air pre-filter pressure drop.
3x0113 | Extract air pre-filter pressure alarm limit. | 0-2000Pa | PV 5.00
Present extract air pre-filter pressure alarm limit.
3x0114 | Extract air pre-filter pressure level, new | 0-2000Pa | PV 5.00
Extract air pre-filter pressure saved from calibration.
3x0115 | Xzone reheat level | 0-100.00% | PV 5.00
Present level of Xzone reheat.
3x0116 | Xzone anti frost temperature | -55.00-125.00°C | PV 5.00
Present Xzone anti frost temperature for water reheating coils.
3x0117 | Xzone cooling level | 0-100.00% | PV 5.00
Present level of Xzone cooling.
3x0118 | Xzone cool step time | 0-600s | PV 5.00
Present time between Xzone cool step shift.
3x0119 | Xzone cool relay 1 restart time | 0-900s | PV 5.00
Present time between two starts of Xzone cool relay 1.
3x0120 | Xzone cool relay 2 restart time | 0-900s | PV 5.00
Present time between two starts of Xzone cool relay 2.
3x0121 | Xzone SA Temp regulator | -55.00-125.00°C | PV 5.00
Present Xzone supply air temperature regulator setpoint.
3x0122 | Xzone EA Temp regulator | -55.00-125.00°C | PV 5.00
Present Xzone extract air temperature regulator setpoint.
3x0123 | Xzone SA Temperature | -55.00-125.00°C | PV 5.00
Present Xzone supply air temperature.
3x0124 | Xzone EA/Room temperature | -55.00-125.00°C | PV 5.00
Present Xzone extract air/room temperature.
3x0125 | Pre-heating air temperature | -55.00-125.00°C | PV 5.00
Present pre-heating air temperature.
3x0126 | Pre-heating level | 0-100.00% | PV 5.00
Present level of pre-heating.
3x0127 | Pre-heating anti frost temperature | -55.00-125.00°C | PV 5.00
Present anti frost temperature for water pre-heating coils.
3x0128 | ReCO2 CO2 input | 0-100.00% | PV 5.00
Present input signal for ReCO2 CO2.
3x0129 | ReCO2 internal damper output | 0-100.00% | PV 5.00
Present output signal for ReCO2 internal damper.
3x0130 | ReCO2 external damper output | 0-100.00% | PV 5.00
Present output signal for ReCO2 external damper.
3x0131 | ReCO2 outdoor airflow | 0-20000l/s | PV 5.00
Present ReCO2 outdoor airflow.
3x0132 | ReCO2 outdoor airflow regulator | 0-20000l/s | PV 5.00
Present ReCO2 outdoor airflow regulator setpoint.
3x0133 | ReCO2 outdoor airflow pressure | 0-2000Pa | PV 5.00
Present ReCO2 outdoor airflow pressure.
3x0134 | Pre-heat operation time | 0-9999 | PV 5.00
Present operation time for pre-heat, measured in minutes and present in days (24h).
3x0135 | Xzone cool operation time | 0-9999 | PV 5.00
Present operation time for Xzone cooling, measured in minutes and present in days (24h).
3x0136 | Xzone reheat operation time | 0-9999 | PV 5.00
Present operation time for Xzone reheat, measured in minutes and present in days (24h).
3x0137 | Supply air-D temperature | -55.00-125.00°C | PV 5.07
Present supply air-D temperature.
3x0138 | Extract air-D temperature | -55.00-125.00°C | PV 5.07
Present extract air-D temperature.
3x0139 | AYC heat temperature | -55.00-125.00°C | PV 5.07
Present AYC heat temperature.
3x0140 | AYC heat temp regulator | -55.00-125.00°C | PV 5.07
Present AYC heat temperature regulator setpoint.
3x0141 | AYC heat valve output | 0-100.00% | PV 5.07
Present level of AYC heat valve output.
3x0142 | Min/Max/Average Sens1Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 1 temperature.
3x0143 | Min/Max/Average Sens2Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 2 temperature.
3x0144 | Min/Max/Average Sens3Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 3 temperature.
3x0145 | Min/Max/Average Sens4Temp | -55.00-125.00°C | PV 5.15
Present Min/Max/Average sensor 4 temperature.
3x0146 | Miru 1 Airflow | 0-10000l/s | PV 6.04
Present Miru 1 airflow.
3x0147 | Miru 1 Airflow regulator | 0-10000l/s | PV 6.04
Present Miru 1 airflow regulator setpoint.
3x0148 | Miru 1 Pressure | 0-750Pa | PV 6.04
Present Miru 1 air duct pressure.
3x0149 | Miru 1 Pressure regulator | 0-750Pa | PV 6.04
Present Miru 1 air duct pressure regulator setpoint.
3x0150 | Miru 1 Outdoor temperature | -55.00-95.00°C | PV 6.04
Present Miru 1 outdoor air temperature.
3x0151 | Miru 1 Operation time | 0-9999 | PV 6.04
Present operation time for Miru 1, measured in minutes and present in days (24h).
3x0152 | Miru 1 Fan level | 0-100.00% | PV 6.04
Present running level for the Miru 1 air fan.
3x0153 | Miru 1 Fan power | 0-6000W | PV 6.04
Present power consumption level for the Miru 1 air fan.
3x0154 | Miru 1 SFP | 0.00-5.00 | PV 6.04
SFP value for Miru 1 air fan.
3x0155 | Miru 1 KWH | 0-999KWH | PV 6.04
KWH value for Miru 1 air fan.
3x0156 | Miru 1 MWH | 0-32000MWH | PV 6.04
MWH value for Miru 1 air fan.
3x0157 | Miru 2 Airflow | 0-10000l/s | PV 6.04
Present Miru 2 airflow.
3x0158 | Miru 2 Airflow regulator | 0-10000l/s | PV 6.04
Present Miru 2 airflow regulator setpoint.
3x0159 | Miru 2 Pressure | 0-750Pa | PV 6.04
Present Miru 2 air duct pressure.
3x0160 | Miru 2 Pressure regulator | 0-750Pa | PV 6.04
Present Miru 2 air duct pressure regulator setpoint.
3x0161 | Miru 2 Outdoor temperature | -55.00-95.00°C | PV 6.04
Present Miru 2 outdoor air temperature.
3x0162 | Miru 2 Operation time | 0-9999 | PV 6.04
Present operation time for Miru 2, measured in minutes and present in days (24h).
3x0163 | Miru 2 Fan level | 0-100.00% | PV 6.04
Present running level for the Miru 2 air fan.
3x0164 | Miru 2 Fan power | 0-6000W | PV 6.04
Present power consumption level for the Miru 2 air fan.
3x0165 | Miru 2 SFP | 0.00-5.00 | PV 6.04
SFP value for Miru 2 air fan.
3x0166 | Miru 2 KWH | 0-999KWH | PV 6.04
KWH value for Miru 2 air fan.
3x0167 | Miru 2 MWH | 0-32000MWH | PV 6.04
MWH value for Miru 2 air fan.
3x0168 | Miru 3 Airflow | 0-10000l/s | PV 6.04
Present Miru 3 airflow.
3x0169 | Miru 3 Airflow regulator | 0-10000l/s | PV 6.04
Present Miru 3 airflow regulator setpoint.
3x0170 | Miru 3 Pressure | 0-750Pa | PV 6.04
Present Miru 3 air duct pressure.
3x0171 | Miru 3 Pressure regulator | 0-750Pa | PV 6.04
Present Miru 3 air duct pressure regulator setpoint.
3x0172 | Miru 3 Outdoor temperature | -55.00-95.00°C | PV 6.04
Present Miru 3 outdoor air temperature.
3x0173 | Miru 3 Operation time | 0-9999 | PV 6.04
Present operation time for Miru 3, measured in minutes and present in days (24h).
3x0174 | Miru 3 Fan level | 0-100.00% | PV 6.04
Present running level for the Miru 3 air fan.
3x0175 | Miru 3 Fan power | 0-6000W | PV 6.04
Present power consumption level for the Miru 3 air fan.
3x0176 | Miru 3 SFP | 0.00-5.00 | PV 6.04
SFP value for Miru 3 air fan.
3x0177 | Miru 3 KWH | 0-999KWH | PV 6.04
KWH value for Miru 3 air fan.
3x0178 | Miru 3 MWH | 0-32000MWH | PV 6.04
MWH value for Miru 3 air fan.
3x0179 | Miru 4 Airflow | 0-10000l/s | PV 6.04
Present Miru 4 airflow.
3x0180 | Miru 4 Airflow regulator | 0-10000l/s | PV 6.04
Present Miru 4 airflow regulator setpoint.
3x0181 | Miru 4 Pressure | 0-750Pa | PV 6.04
Present Miru 4 air duct pressure.
3x0182 | Miru 4 Pressure regulator | 0-750Pa | PV 6.04
Present Miru 4 air duct pressure regulator setpoint.
3x0183 | Miru 4 Outdoor temperature | -55.00-95.00°C | PV 6.04
Present Miru 4 outdoor air temperature.
3x0184 | Miru 4 Operation time | 0-9999 | PV 6.04
Present operation time for Miru 4, measured in minutes and present in days (24h).
3x0185 | Miru 4 Fan level | 0-100.00% | PV 6.04
Present running level for the Miru 4 air fan.
3x0186 | Miru 4 Fan power | 0-6000W | PV 6.04
Present power consumption level for the Miru 4 air fan.
3x0187 | Miru 4 SFP | 0.00-5.00 | PV 6.04
SFP value for Miru 4 air fan.
3x0188 | Miru 4 KWH | 0-999KWH | PV 6.04
KWH value for Miru 4 air fan.
3x0189 | Miru 4 MWH | 0-32000MWH | PV 6.04
MWH value for Miru 4 air fan.
3x0190 | Miru 5 Airflow | 0-10000l/s | PV 6.04
Present Miru 5 airflow.
3x0191 | Miru 5 Airflow regulator | 0-10000l/s | PV 6.04
Present Miru 5 airflow regulator setpoint.
3x0192 | Miru 5 Pressure | 0-750Pa | PV 6.04
Present Miru 5 air duct pressure.
3x0193 | Miru 5 Pressure regulator | 0-750Pa | PV 6.04
Present Miru 5 air duct pressure regulator setpoint.
3x0194 | Miru 5 Outdoor temperature | -55.00-95.00°C | PV 6.04
Present Miru 5 outdoor air temperature.
3x0195 | Miru 5 Operation time | 0-9999 | PV 6.04
Present operation time for Miru 5, measured in minutes and present in days (24h).
3x0196 | Miru 5 Fan level | 0-100.00% | PV 6.04
Present running level for the Miru 5 air fan.
3x0197 | Miru 5 Fan power | 0-6000W | PV 6.04
Present power consumption level for the Miru 5 air fan.
3x0198 | Miru 5 SFP | 0.00-5.00 | PV 6.04
SFP value for Miru 5 air fan.
3x0199 | Miru 5 KWH | 0-999KWH | PV 6.04
KWH value for Miru 5 air fan.
3x0200 | Miru 5 MWH | 0-32000MWH | PV 6.04
MWH value for Miru 5 air fan.
3x0201 | Miru 6 Airflow | 0-10000l/s | PV 6.04
Present Miru 6 airflow.
3x0202 | Miru 6 Airflow regulator | 0-10000l/s | PV 6.04
Present Miru 6 airflow regulator setpoint.
3x0203 | Miru 6 Pressure | 0-750Pa | PV 6.04
Present Miru 6 air duct pressure.
3x0204 | Miru 6 Pressure regulator | 0-750Pa | PV 6.04
Present Miru 6 air duct pressure regulator setpoint.
3x0205 | Miru 6 Outdoor temperature | -55.00-95.00°C | PV 6.04
Present Miru 6 outdoor air temperature.
3x0206 | Miru 6 Operation time | 0-9999 | PV 6.04
Present operation time for Miru 6, measured in minutes and present in days (24h).
3x0207 | Miru 6 Fan level | 0-100.00% | PV 6.04
Present running level for the Miru 6 air fan.
3x0208 | Miru 6 Fan power | 0-6000W | PV 6.04
Present power consumption level for the Miru 6 air fan.
3x0209 | Miru 6 SFP | 0.00-5.00 | PV 6.04
SFP value for Miru 6 air fan.
3x0210 | Miru 6 KWH | 0-999KWH | PV 6.04
KWH value for Miru 6 air fan.
3x0211 | Miru 6 MWH | 0-32000MWH | PV 6.04
MWH value for Miru 6 air fan.
3x0212 | Miru 7 Airflow | 0-10000l/s | PV 6.04
Present Miru 7 airflow.
3x0213 | Miru 7 Airflow regulator | 0-10000l/s | PV 6.04
Present Miru 7 airflow regulator setpoint.
3x0214 | Miru 7 Pressure | 0-750Pa | PV 6.04
Present Miru 7 air duct pressure.
3x0215 | Miru 7 Pressure regulator | 0-750Pa | PV 6.04
Present Miru 7 air duct pressure regulator setpoint.
3x0216 | Miru 7 Outdoor temperature | -55.00-95.00°C | PV 6.04
Present Miru 7 outdoor air temperature.
3x0217 | Miru 7 Operation time | 0-9999 | PV 6.04
Present operation time for Miru 7, measured in minutes and present in days (24h).
3x0218 | Miru 7 Fan level | 0-100.00% | PV 6.04
Present running level for the Miru 7 air fan.
3x0219 | Miru 7 Fan power | 0-6000W | PV 6.04
Present power consumption level for the Miru 7 air fan.
3x0220 | Miru 7 SFP | 0.00-5.00 | PV 6.04
SFP value for Miru 7 air fan.
3x0221 | Miru 7 KWH | 0-999KWH | PV 6.04
KWH value for Miru 7 air fan.
3x0222 | Miru 7 MWH | 0-32000MWH | PV 6.04
MWH value for Miru 7 air fan.
3x0223 | Miru 8 Airflow | 0-10000l/s | PV 6.04
Present Miru 8 airflow.
3x0224 | Miru 8 Airflow regulator | 0-10000l/s | PV 6.04
Present Miru 8 airflow regulator setpoint.
3x0225 | Miru 8 Pressure | 0-750Pa | PV 6.04
Present Miru 8 air duct pressure.
3x0226 | Miru 8 Pressure regulator | 0-750Pa | PV 6.04
Present Miru 8 air duct pressure regulator setpoint.
3x0227 | Miru 8 Outdoor temperature | -55.00-95.00°C | PV 6.04
Present Miru 8 outdoor air temperature.
3x0228 | Miru 8 Operation time | 0-9999 | PV 6.04
Present operation time for Miru 8, measured in minutes and present in days (24h).
3x0229 | Miru 8 Fan level | 0-100.00% | PV 6.04
Present running level for the Miru 8 air fan.
3x0230 | Miru 8 Fan power | 0-6000W | PV 6.04
Present power consumption level for the Miru 8 air fan.
3x0231 | Miru 8 SFP | 0.00-5.00 | PV 6.04
SFP value for Miru 8 air fan.
3x0232 | Miru 8 KWH | 0-999KWH | PV 6.04
KWH value for Miru 8 air fan.
3x0233 | Miru 8 MWH | 0-32000MWH | PV 6.04
MWH value for Miru 8 air fan.
3x0234 | Miru 9 Airflow | 0-10000l/s | PV 6.04
Present Miru 9 airflow.
3x0235 | Miru 9 Airflow regulator | 0-10000l/s | PV 6.04
Present Miru 9 airflow regulator setpoint.
3x0236 | Miru 9 Pressure | 0-750Pa | PV 6.04
Present Miru 9 air duct pressure.
3x0237 | Miru 9 Pressure regulator | 0-750Pa | PV 6.04
Present Miru 9 air duct pressure regulator setpoint.
3x0238 | Miru 9 Outdoor temperature | -55.00-95.00°C | PV 6.04
Present Miru 9 outdoor air temperature.
3x0239 | Miru 9 Operation time | 0-9999 | PV 6.04
Present operation time for Miru 9, measured in minutes and present in days (24h).
3x0240 | Miru 9 Fan level | 0-100.00% | PV 6.04
Present running level for the Miru 9 air fan.
3x0241 | Miru 9 Fan power | 0-6000W | PV 6.04
Present power consumption level for the Miru 9 air fan.
3x0242 | Miru 9 SFP | 0.00-5.00 | PV 6.04
SFP value for Miru 9 air fan.
3x0243 | Miru 9 KWH | 0-999KWH | PV 6.04
KWH value for Miru 9 air fan.
3x0244 | Miru 9 MWH | 0-32000MWH | PV 6.04
MWH value for Miru 9 air fan.
3x0245 | Miru 10 Airflow | 0-10000l/s | PV 6.04
Present Miru 10 airflow.
3x0246 | Miru 10 Airflow regulator | 0-10000l/s | PV 6.04
Present Miru 10 airflow regulator setpoint.
3x0247 | Miru 10 Pressure | 0-750Pa | PV 6.04
Present Miru 10 air duct pressure.
3x0248 | Miru 10 Pressure regulator | 0-750Pa | PV 6.04
Present Miru 10 air duct pressure regulator setpoint.
3x0249 | Miru 10 Outdoor temperature | -55.00-95.00°C | PV 6.04
Present Miru 10 outdoor air temperature.
3x0250 | Miru 10 Operation time | 0-9999 | PV 6.04
Present operation time for Miru 10, measured in minutes and present in days (24h).
3x0251 | Miru 10 Fan level | 0-100.00% | PV 6.04
Present running level for the Miru 10 air fan.
3x0252 | Miru 10 Fan power | 0-6000W | PV 6.04
Present power consumption level for the Miru 10 air fan.
3x0253 | Miru 10 SFP | 0.00-5.00 | PV 6.04
SFP value for Miru 10 air fan.
3x0254 | Miru 10 KWH | 0-999KWH | PV 6.04
KWH value for Miru 10 air fan.
3x0255 | Miru 10 MWH | 0-32000MWH | PV 6.04
MWH value for Miru 10 air fan.
3x0256 | BB Operation mode | 0-2 | PV 6.05
Present Blue Box operation mode. 0=Stop 1=Heat 2=Cool
3x0257 | BB Cool temp regulator | -40.0-176.0°C | PV 6.05
Present Blue Box cool temperature regulator setpoint.
3x0258 | BB Heat temp regulator | -40.0-176.0°C | PV 6.05
Present Blue Box heat temperature regulator setpoint.
3x0259 | BB Supply water temperature | -20.0-80.0°C | PV 6.05
Present Blue Box supply water temperature.
3x0260 | BB Return water temperature | -40.0-176.0°C | PV 6.05
Present Blue Box return water temperature.
3x0261 | BB Supply pre-coil temperature | -20.0-80.0°C | PV 6.05
Present Blue Box pre-coil water temperature.
3x0262 | Extended ext. reg. seq. frost temp | -55.00-125.00°C | PV 6.07
Present extended extra regulation sequence frost temperature.
3x0263 | Extended ext. reg. seq. Output | 0-100.00% | PV 6.07
Present extended extra regulation sequence output.
3x0264 | Steam humid output | 0-100.00% | PV 6.07
Present steam humidification output.
3x0265 | End-filter pressure level | 0-2000Pa | PV 6.07
Present supply air end-filter pressure drop.
3x0266 | End-filter pressure level, new | 0-2000Pa | PV 6.07
Supply air end-filter pressure saved from calibration.
3x0267 | End-filter pressure alarm limit | 0-2000Pa | PV 6.07
Present supply air end-filter pressure alarm limit.

## Holding Registers
GB.ModBus480.120417
Holding Registers. 16-bit integer value (R/W).
Modbus | Name | Min/Max | Misc
4x0001 | SA Low speed airflow setpoint | 0-8200l/s
Supply airflow setpoint for the unit when running in low speed operation.
4x0002 | SA High speed airflow setpoint | 0-8200l/s
Supply airflow setpoint for the unit when running in high speed operation.
4x0003 | SA Max speed airflow setpoint | 0-8200l/s
Supply airflow max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
4x0004 | SA Min speed airflow setpoint | 0-8200l/s
Supply airflow min. limit for the unit when the low/high speed operation setpoint is altered when running in fan regulation mode VAV demand.
4x0005 | EA Low speed airflow setpoint | 0-8200l/s
Extract airflow setpoint for the unit when running in low speed operation.
4x0006 | EA High speed airflow setpoint | 0-8200l/s
Extract airflow setpoint for the unit when running in high speed operation.
4x0007 | EA Max speed airflow setpoint | 0-8200l/s
Extract airflow max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
4x0008 | EA Min speed airflow setpoint | 0-8200l/s
Extract airflow min. limit for the unit when the low/high speed operation setpoint is altered when running in fan regulation mode VAV demand.
4x0009 | SA Low speed pressure setpoint | 0-750Pa
Supply air duct pressure setpoint for the unit when running in low speed operation.
4x0010 | SA High speed pressure setpoint | 20-750Pa
Supply air duct pressure for the unit when running in high speed operation.
4x0011 | SA Max speed output signal | 10.00-100.00%
Max. limit for the supply air fan speed when running in pressure regulation mode.
4x0012 | SA Max speed pressure setpoint | 20-750Pa
Supply air duct pressure max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
4x0013 | EA Low speed pressure setpoint | 0-750Pa
Extract air duct pressure setpoint for the unit when running in low speed operation.
4x0014 | EA High speed pressure setpoint | 20-750Pa
Extract air duct pressure setpoint for the unit when running in high speed operation.
4x0015 | EA Max speed output signal | 10.00-100.00%
Max. limit for the extract air fan speed when running in pressure regulation mode.
4x0016 | EA Max speed pressure setpoint | 20-750Pa
Extract air duct pressure max. limit for the unit when the low/high speed operation setpoint is altered by boosting function etc.
4x0017 | SA Low speed demand setpoint | 0-100.00%
Supply air setpoint for the 0-10V input signal on terminal 30..31 for the unit when running in low speed operation.
4x0018 | SA High speed demand setpoint | 0-100.00%
Supply air setpoint for the 0-10V input signal on terminal 30..31 for the unit when running in high speed operation.
4x0019 | EA Low speed demand setpoint | 0-100.00%
Extract air setpoint for the 0-10V input signal on terminal 32..33 for the unit when running in low speed operation.
4x0020 | EA High speed demand setpoint | 0-100.00%
Extract air setpoint for the 0-10V input signal on terminal 32..33 for the unit when running in high speed operation.
4x0021 | SA Airflow regulation zone | 1.00 - 10.00
Supply airflow regulation zone setting in % of the present airflow setpoint that the regulator is allowed to work within.
4x0022 | SA Airflow C-factor | 0.005 - 2.500
Supply airflow regulator affection setting.
4x0023 | EA Airflow regulation zone | 1.00 - 10.00
Extract airflow regulation zone setting in % of the present airflow setpoint that the regulator is allowed to work within.
4x0024 | EA Airflow C-factor | 0.005 - 2.500
Extract airflow regulator affection setting.
4x0025 | SA Pressure regulation zone | 1.00 - 10.00
Supply air pressure regulation zone setting in % of the present duct pressure setpoint that the regulator is allowed to work within.
4x0026 | SA Pressure C-factor | 0.005 - 2.500
Supply air pressure regulator affection setting.
4x0027 | EA Pressure regulation zone | 1.00 - 10.00
Extract air pressure regulation zone setting in % of the present duct pressure setpoint that the regulator is allowed to work within.
4x0028 | EA Pressure C-factor | 0.005 - 2.500
Extract air pressure regulator affection setting.
4x0029 | SA Demand P-band. | 1.00 - 100.00
Supply air demand regulator P-band setting.
4x0030 | SA Demand C-factor | 0.005 - 2.500
Supply air demand regulator affection setting.
4x0031 | EA Demand P-band. | 1.00 - 100.00
Extract air demand regulator P-band setting.
4x0032 | EA Demand C-factor | 0.005 - 2.500
Extract air demand regulator affection setting.
4x0033 | ERS 1 Diff | 1.00 - 7.00°C
Supply air temperature difference setting according to the diagram for ERS 1.
4x0034 | ERS 1 Breakpoint | 12.00 - 26.00°C
Breakpoint setting according to the diagram for ERS 1.
4x0035 | ERS 2 Breakpoint X1 | 10.00-38.00°C
Breakpoint X1 setting according to the diagram for ERS 2.
4x0036 | ERS 2 Breakpoint Y1 | 10.00-40.00°C
Breakpoint Y1 setting according to the diagram for ERS 2.
4x0037 | ERS 2 Breakpoint X2 | 11.00-39.00°C
Breakpoint X2 setting according to the diagram for ERS 2.
4x0038 | ERS 2 Breakpoint Y2 | 10.00-40.00°C
Breakpoint Y2 setting according to the diagram for ERS 2.
4x0039 | ERS 2 Breakpoint X3 | 12.00-40.00°C
Breakpoint X3 setting according to the diagram for ERS 2.
4x0040 | ERS 2 Breakpoint Y3 | 10.00-40.00°C
Breakpoint Y3 setting according to the diagram for ERS 2.
4x0041 | SA Temperature setpoint | 10.00-40.00°C
Supply air temperature setting, for supply air temp regulation mode.
4x0042 | EA/Room Temperature setpoint | 10.00-40.00°C
Extract air/room temperature setting, for Extract air/room temp regulation mode.
4x0043 | SA Min temp setpoint | 8.00-20.00°C
Supply air min.setpoint during EA/room regulation mode.
4x0044 | SA Max temp setpoint | 16.00-50.00°C
Supply air max.setpoint during EA/room regulation mode.
4x0045 | SA Temperature P-band | 1.00 - 40.00 | PV 5.00
Supply air temperature regulator P-band setting.
4x0046 | EA/Room Temperature P-band | 1.00 - 40.00 | PV 5.00
Extract air/room temperature regulator P-band setting.
4x0047 | SA HX. Reg C-factor | 0.000 - 2.500
Supply air heat exchange regulator affection setting.
4x0048 | EA/Room HX. Reg C-factor | 0.000 - 2.500
Extract air/room heat exchange regulator affection setting.
4x0049 | SA Heat Reg C-factor | 0.000 - 2.500
Supply air reheat regulator affection setting.
4x0050 | EA/Room Heat Reg C-factor | 0.000 - 2.500
Extract air/room reheat regulator affection setting.
4x0051 | SA Extra Reg heat C-factor | 0.000 - 2.500
Supply air extra regulation sequence for reheating regulator affection setting.
4x0052 | SA Extra Reg cool C-factor | 0.000 - 2.500
Supply air extra regulation sequence for cooling regulator affection setting.
4x0053 | EA Extra Reg heat C-factor | 0.000 - 2.500
Extract air extra regulation sequence for reheating regulator affection setting.
4x0054 | EA Extra Reg cool C-factor | 0.000 - 2.500
Extract air extra regulation sequence for cooling regulator affection setting.
4x0055 | SA Down regulation Reg C-factor | 0.000 - 2.500
Supply air reheat regulator affection setting.
4x0056 | Reserve
4x0057 | SA Cool reg C-factor | 0.000 - 2.500
Supply air cool regulator affection setting.
4x0058 | EA/Room Cool reg C-factor | 0.000 - 2.500
Extract air/room cool regulator affection setting.
4x0059 | SA Cooling boost C-factor | 0.000 - 2.500
Supply air cooling boost affection setting.
4x0060 | EA/Room Cooling boost reg C-factor | 0.000 - 2.500
Extract air/room cooling boost regulator affection setting.
4x0061 | HX Pressure alarm set. | 30 - 100Pa
Heat exchange pressure alarm limit setting (alarm no.38).
4x0062 | P/C.HX. defrost P-band | 1.00 - 40.00 | PV 2.00
Plate/coil heat exchange defrost P-band setting.
4x0063 | P/C.HX. defrost C-factor | 0.000 - 2.500 | PV 2.00
Plate/coil heat exchange defrost C-factor setting.
4x0064 | Cooling off set. | 10 - 50%
Cooling off airflow setting in % of max. airflow.
4x0065 | SA Down regulation neutral zone | 0.00-10.00°C
Neutral zone setting before downregulation is permitted.
4x0066 | Cool Outdoor temp limit.1 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 1.
4x0067 | Cool Outdoor temp limit.2 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 2.
4x0068 | Cool Outdoor temp limit.3 | 0.00-25.00°C
Outdoor temperature limit setting for cooling stage 3.
4x0069 | Temperature reg. Neutral zone | 0.50-10.00°C
Neutral zone setting before shift between heating and cooling.
4x0070 | SA Cool min air flow | 0-8200l/s
Supply air min. air flow setting for cooling.
4x0071 | EA Cool min air flow | 0-8200l/s
Extract air min. air flow setting for cooling.
4x0072 | Heating boost start limit | 0.00-40.00°C
Heating boost start temperature limit.
4x0073 | Cooling boost start limit | 0.00-40.00°C
Cooling boost (comfort) start temperature limit.
4x0074 | SA Filter alarm limit | 50-300Pa
Supply air filter pressure alarm limit setting.
4x0075 | EA Filter alarm limit | 50-300Pa
Extract air filter pressure alarm limit setting.
4x0076 | Int. Night heat room start temp | 5.00-25.00°C
Intermittent night heat function, extract air temperature setting for start.
4x0077 | Int. Night heat room stop temp | 5.00-25.00°C
Intermittent night heat function, extract air temperature setting for stop.
4x0078 | Int. Night heat SA temp setpoint | 5.00-40.00°C
Intermittent night heat function, supply air temperature setpoint during night heat.
4x0079 | Int. Night heat SA airflow setpoint | 0-8200l/s
Intermittent night heat function, supply airflow setpoint during night heat.
4x0080 | Int. Night heat EA airflow setpoint | 0-8200l/s
Intermittent night heat function, extract airflow setpoint during night heat.
4x0081 | Summer night cool EA start temp | 17.00-27.00°C
Summer night cool function, extract air temperature setting for start.
4x0082 | Summer night cool EA stop temp | 12.00-22.00°C
Summer night cool function, extract air temperature setting for stop.
4x0083 | Summer night cool outdoor temp limit | 5.00-15.00°C
Summer night cool function, outdoor temperature limit.
4x0084 | Summer night cool SA temp setpoint | 10.00-20.00°C
Summer night cool function, supply air temperature setpoint during summer night cool.
4x0085 | Outdoor temp comp. Winter X1. | -30.00-(-10.00)°C
Endpoint of winter compensation.
4x0086 | Outdoor temp comp. Winter X2. | -10.00-15.00°C
Startpoint of winter compensation.
4x0087 | Outdoor temp comp. Winter Y1. | 0.00-10.00°C
Level of winter compensation at X1.
4x0088 | Outdoor temp comp. Summer X3. | 15.00-25.00°C
Startpoint of summer compensation.
4x0089 | Outdoor temp comp. Summer X4. | 25.00-40.00°C
Endpoint of summer compensation.
4x0090 | Outdoor temp comp. Summer Y2. | -10.00-10.00°C
Level of summer compensation at X4.
4x0091 | Outdoor airflow comp. Winter X1. | -30.00-(-10.00)°C
Endpoint of winter compensation.
4x0092 | Outdoor airflow comp. Winter X2. | -10.00-15.00°C
Startpoint of winter compensation.
4x0093 | Outdoor airflow comp. Winter Y1. | 0-50.00%
Level of airflow compensation at X1.
4x0094 | Extra Reg. Sequence max output | 0-100.00%
Maximum output signal setting for the extra regulation sequence.
4x0095 | EA/Room min temp alarm limit | 8.00-20.00°C
Setting for min extract air /room temp alarm no.40.
4x0096 | SA Deviation alarm limit | 2.00-15.00°C
Setting for supply air temperature below present setpoint, alarm no.41.
4x0097 | Reserve
4x0098 | SA Fan regulation mode | 0 - 3
Setting of regulation type for the supply air fan. 0=Airflow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by EA fan.
4x0099 | EA Fan regulation mode | 0 - 3
Setting of regulation type for the extract air fan. 0=Airflow reg. 1=Pressure reg. 2=Demand reg. 3=Slave controlled by SA fan.
4x0100 | ERS Step | 1 - 4
Setting of curve when temperature is above breakpoint.
4x0101 | Temperature regulation mode. | 0 - 3
Setting of temperature regulation type. 0=ERS 1 reg. 1=ERS 2 reg. 2=SA reg. 3=EA/Room reg.
4x0102 | Cooling off period | 60 - 900s
Time setting for cooling off electrical heating coil.
4x0103 | Cool step time | 0 - 600s
Time setting between cool step shift.
4x0104 | Cool restart time | 60 - 900s
Setting of time between two starts of the cool relays.
4x0105 | Cool regulation mode | 0 - 6 | PV 3.00
Setting of cool regulation type 0=Controlled 0-10V 1=Controlled 10-0V 2=On/Off 1-step 3=On/Off 2-steps 4=On/Off 3-steps binary 5=CoolDX economy (PV 2.00) 6=CoolDX comfort (PV 3.00)
4x0106 | Heating boost regulation mode. | 0 - 1
Setting for heating boost function. 0=Inactive. 1=Active.
4x0107 | Cooling boost regulation mode. | 0 - 5 | PV 5.00
Setting of cooling boost regulation type. 0=Inactive. 1=Comfort. 2=Economy. 3=Sequence. 4=Comfort+economy (New in PV 5.00). 5=Economy+sequence (New in PV 5.00).
4x0108 | Filter calibration mode | 0 - 5 | PV 5.00
Setting for required filter calibration. 0=Inactive. 1=SA+EA-Filter. 2=SA-Filter. 3=EA-Filter. 4=HX. 5=ReCO2 (New in PV 5.00).
4x0109 | Air adjustment time, minutes | 0 - 1727
Setting for amount of minutes to air adjustment function.
4x0110 | Air adjustment time, hours | 0 - 28
Setting for amount of hours to air adjustment function.
4x0111 | Hand held terminal language | 0 - 18 | PV 5.01
0=Svenska 1=Norsk 2=Dansk 3=Suomi 4=English 5=Français 6=Deutsch 7=Polski 8=Český 9=Italiano 10=Español 11=Português 12=Pycckий 13=Eesti 14=Latviesu 15=Lietiviu 16=Nederlands 17=Magyar (New in PV 5.00) 18=Türkçe (New in PV 5.01)
4x0112 | Summer night cool start, hour | 0-23
Setting for start time of summer night cooling function.
4x0113 | Summer night cool start, minute | 0-59
Setting for start time of summer night cooling function.
4x0114 | Summer night cool stop, hour | 0-23
Setting for stop time of summer night cooling function.
4x0115 | Summer night cool stop, minute | 0-59
Setting for stop time of summer night cooling function.
4x0116 | Extra regulation sequence cool mode | 0 - 2
Setting of extra regulation sequence cool type. 0=Inactive. 1=Comfort. 2=Economy.
4x0117 | Extra regulation sequence heat mode | 0 - 2
Setting of extra regulation sequence heat type. 0=Inactive. 1=Comfort. 2=Economy.
4x0118 | Morning boost time, hours | 0-23
Setting of morning boost time before normal operation.
4x0119 | Morning boost time, minutes | 0-59
Setting of morning boost time before normal operation.
4x0120 | Startup time | 0 - 600s
Setting of time for startup when the unit regulator is running with fixed signals.
4x0121 | Start delay SA fan. | 0 - 600s
Setting of start delay time for the supply air fan.
4x0122 | Start delay EA fan. | 0 - 600s
Setting of start delay time for the extract air fan after supply air fan has started.
4x0123 | Air flow unit | 0 -2
Setting of air flow unit presented in the unit's hand held terminal and WEB. 0=l/s. 1=m3/s. 2=m3/h.
4x0124 | Reserve |  | PV 3.00
4x0125 | Year | 2000-2099
Setting for the unit's internal clock.
4x0126 | Month | 1-12
Setting for the unit's internal clock.
4x0127 | Date | 0-31
Setting for the unit's internal clock.
4x0128 | Hour | 0-23
Setting for the unit's internal clock.
4x0129 | Minute | 0-59
Setting for the unit's internal clock.
4x0130 | Second | 0-59
Setting for the unit's internal clock.
4x0131 | Time channel 1 status | 0-10,16-26
Low speed High speed 0=Inactive 16=Inactive 1=Monday 17=Monday 2=Tuesday 18=Tuesday 3=Wednesday 19=Wednesday 4=Thursday 20=Thursday 5=Friday 21=Friday 6=Saturday 22=Saturday 7=Sunday 23=Sunday 8=Monday..Friday 24=Monday..Friday 9=Monday..Sunday 25=Monday..Sunday 10=Saturday..Sunday 26=Saturday..Sunday
4x0132 | Time channel 1 start hour | 0-23
4x0133 | Time channel 1 start minute | 0-59
4x0134 | Time channel 1 stop hour | 0-23
4x0135 | Time channel 1 stop minute | 0-59
4x0136 | Time channel 2 status | 0-10,16-26
4x0137 | Time channel 2 start hour | 0-23
4x0138 | Time channel 2 start minute | 0-59
4x0139 | Time channel 2 stop hour | 0-23
4x0140 | Time channel 2 stop minute | 0-59
4x0141 | Time channel 3 status | 0-10,16-26
4x0142 | Time channel 3 start hour | 0-23
4x0143 | Time channel 3 start minute | 0-59
4x0144 | Time channel 3 stop hour | 0-23
4x0145 | Time channel 3 stop minute | 0-59
4x0146 | Time channel 4 status | 0-10,16-26
4x0147 | Time channel 4 start hour | 0-23
4x0148 | Time channel 4 start minute | 0-59
4x0149 | Time channel 4 stop hour | 0-23
4x0150 | Time channel 4 stop minute | 0-59
4x0151 | Time channel 5 status | 0-10,16-26
4x0152 | Time channel 5 start hour | 0-23
4x0153 | Time channel 5 start minute | 0-59
4x0154 | Time channel 5 stop hour | 0-23
4x0155 | Time channel 5 stop minute | 0-59
4x0156 | Time channel 6 status | 0-10,16-26
4x0157 | Time channel 6 start hour | 0-23
4x0158 | Time channel 6 start minute | 0-59
4x0159 | Time channel 6 stop hour | 0-23
4x0160 | Time channel 6 stop minute | 0-59
4x0161 | Time channel 7 status | 0-10,16-26
4x0162 | Time channel 7 start hour | 0-23
4x0163 | Time channel 7 start minute | 0-59
4x0164 | Time channel 7 stop hour | 0-23
4x0165 | Time channel 7 stop minute | 0-59
4x0166 | Time channel 8 status | 0-10,16-26
4x0167 | Time channel 8 start hour | 0-23
4x0168 | Time channel 8 start minute | 0-59
4x0169 | Time channel 8 stop hour | 0-23
4x0170 | Time channel 8 stop minute | 0-59
4x0171 | Extended low speed op. Hours | 0-23
Setting for extended low speed operation.
4x0172 | Extended low speed op. Minutes | 0-59
Setting for extended low speed operation.
4x0173 | Extended high speed op. Hours | 0-23
Setting for extended low speed operation.
4x0174 | Extended high speed op. Minutes | 0-59
Setting for extended low speed operation.
4x0175 | Communication operation mode | 0 - 4 | PV 5.00
Setting of unit operation mode from communication. 0=Auto operation (Normal stop when time channels are deactivated). 1=Communication stop 1. 2=Communication low speed. 3=Communication high speed. 4=Communication stop 2 (New in PV 5.00). Intermittent night heat and morning boost functions works at stop 2.
4x0176 | Service period alarm. | 0-99
Setting for delay time in months before service alarm.
4x0177 | External alarm 1 delay | 1 - 600s
Setting of delay time for external alarm no 1
4x0178 | External alarm 2 delay | 1 - 600s
Setting of delay time for external alarm no 2
4x0179 | Int. Night heat SA pressure setpoint | 20-750Pa
Intermittent night heat function, supply pressure setpoint during night heat.
4x0180 | Int. Night heat EA pressure setpoint | 20-750Pa
Intermittent night heat function, extract pressure setpoint during night heat.
4x0181 | Copy of Coil Status 1-16 | 0-65535
Bit 0=1x0001 Bit 1=1x0002 Bit 15=1x0016
4x0182 | Copy of Coil Status 17-32 | 0-65535
Bit 0=1x00017 Bit 1=1x00018 Bit 15=1x0032
4x0183 | Copy of Coil Status 33-48 | 0-65535
Bit 0=1x00033 Bit 1=1x00034 Bit 15=1x0048
4x0184 | Heat relay periodic func. | 0-3 | PV 2.02
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
4x0185 | Cool relay 1 periodic func. | 0-3 | PV 2.02
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
4x0186 | Cool relay 2 periodic func. | 0-3 | PV 2.02
Setting of periodic operation. 0=Inactive 1=Pump 2=Pump+valve 3=Valve (PV 2.02)
4x0187 | Slave control C-factor | 0.5 - 2.0 | PV 5.07
Slave regulator affection setting.
4x0188 | SA dehumid P-band | 1.00 - 40.00 | PV 5.00
SA dehumid regulator P-band setting.
4x0189 | SA dehumid C-factor | 0.000 - 2.500
SA dehumid regulator affection setting.
4x0190 | Dewpoint reg. P-band | 1.00 - 40.00 | PV 5.00
Dewpoint regulator P-band setting.
4x0191 | Dewpoint reg. C-factor | 0.000 - 2.500
Dewpoint regulator affection setting.
4x0192 | AYC chilled water temperature | 5.00-30.00°C
Setting of AYC chilled water temperature setpoint.
4x0193 | Dewpoint neutral zone | 0.00-5.00°C
Dewpoint neutral zone setting.
4x0194 | Comp. airflow | 0-30.00%
Setting of comp. airflow.
4x0195 | Supply air-humidity | 10.00-90.00%
Setting of supply air-humidity.
4x0196 | Water heating periodic op. time | 0-60min
Setting of periodic op. time (minute).
4x0197 | Water heating interval | 0-168h
Setting of water heating interval time (hour).
4x0198 | Cool periodic op. time | 0-60min | PV 2.02
Setting of periodic op. time (minute).
4x0199 | Cool interval | 0-168h | PV 2.02
Setting of cool interval time (hour).
4x0200 | P/C.HX. bypass adj. | -5.00-5.00°C | PV 2.02
Setting of plate/coil heat exchange bypass adjustment.
4x0201 | EA/Room temperature (external) func. | 0-3 | PV 5.15
Setting of EA/Room temperature (external) function. 0=Inactive. 1=Input signal on terminal 40..41. 2=Communication (4x0202). 3=Min/Max/Average (PV 5.15).
4x0202 | EA/Room temperature com. | -55.00-125.00°C | PV 3.00
Setting of EA/Room temperature via communication.
4x0203 | Outdoor temperature (external) func. | 0-2 | PV 3.00
Setting of outdoor temperature (external) function. 0=Inactive. 1=Input signal on terminal 38..39. 2=Communication (4x0204).
4x0204 | Outdoor temperature com. | -55.00-125.00°C | PV 3.00
Setting of outdoor temperature via communication.
4x0205 | Timeout temperature com. | 0-9999min | PV 3.00
Setting of timeout for temperature via communication (4x0202, 4x0204).
4x0206 | Flow at fire function. | 0-3 | PV 3.00
Setting for activating the air fan operation at fire function 0=Inactive. 1=SA. 2=EA. 3=SA+EA.
4x0207 | Air fan down regulation func. | 0-2 | PV 3.00
Setting for activating the air fan down regulation function 0=Inactive. 1=SA. 2=SA+EA.
4x0208 | SA speed at fire. | 50.00-100.00% | PV 3.00
Setting of supply air speed at fire.
4x0209 | EA speed at fire. | 50.00-100.00% | PV 3.00
Setting of extract air speed at fire.
4x0210 | Temperature alarm setpoint. | -25.00-25.00°C | PV 3.00
Temperature alarm function setting (no.80).
4x0211 | Temperature alarm time. | 1-999s | PV 3.00
Setting of delay time for temperature alarm (no.80).
4x0212 | Supply air min P-band. | 1.00 - 40.00 | PV 3.00
Supply air min regulator P-band setting.
4x0213 | Supply air min C-factor. | 0.000 - 2.500 | PV 3.00
Supply air min regulator affection setting.
4x0214 | Supply air max P-band. | 1.00 - 40.00 | PV 3.00
Supply air max regulator P-band setting.
4x0215 | Supply air max C-factor. | 0.000 - 2.500 | PV 3.00
Supply air max regulator affection setting.
4x0216 | Year channel 1 function. | 0 - 3 | PV 3.00
0=Inactive. 1=Stop. 2=Low speed. 3=High speed.
4x0217 | Year channel 1 start year. | 2000 - 2099 | PV 3.00
4x0218 | Year channel 1 start month. | 1 - 12 | PV 3.00
4x0219 | Year channel 1 start date. | 1 - 31 | PV 3.00
4x0220 | Year channel 1 start hour. | 0 - 23 | PV 3.00
4x0221 | Year channel 1 start minute. | 0 - 59 | PV 3.00
4x0222 | Year channel 1 stop year. | 2000 - 2099 | PV 3.00
4x0223 | Year channel 1 stop month. | 1 - 12 | PV 3.00
4x0224 | Year channel 1 stop date. | 1 - 31 | PV 3.00
4x0225 | Year channel 1 stop hour. | 0 - 23 | PV 3.00
4x0226 | Year channel 1 stop minute. | 0 - 59 | PV 3.00
4x0227 | Year channel 2 function. | 0 - 3 | PV 3.00
4x0228 | Year channel 2 start year. | 2000 - 2099 | PV 3.00
4x0229 | Year channel 2 start month. | 1 - 12 | PV 3.00
4x0230 | Year channel 2 start date. | 1 - 31 | PV 3.00
4x0231 | Year channel 2 start hour. | 0 - 23 | PV 3.00
4x0232 | Year channel 2 start minute. | 0 - 59 | PV 3.00
4x0233 | Year channel 2 stop year. | 2000 - 2099 | PV 3.00
4x0234 | Year channel 2 stop month. | 1 - 12 | PV 3.00
4x0235 | Year channel 2 stop date. | 1 - 31 | PV 3.00
4x0236 | Year channel 2 stop hour. | 0 - 23 | PV 3.00
4x0237 | Year channel 2 stop minute. | 0 - 59 | PV 3.00
4x0238 | Year channel 3 function. | 0 - 3 | PV 3.00
4x0239 | Year channel 3 start year. | 2000 - 2099 | PV 3.00
4x0240 | Year channel 3 start month. | 1 - 12 | PV 3.00
4x0241 | Year channel 3 start date. | 1 - 31 | PV 3.00
4x0242 | Year channel 3 start hour. | 0 - 23 | PV 3.00
4x0243 | Year channel 3 start minute. | 0 - 59 | PV 3.00
4x0244 | Year channel 3 stop year. | 2000 - 2099 | PV 3.00
4x0245 | Year channel 3 stop month. | 1 - 12 | PV 3.00
4x0246 | Year channel 3 stop date. | 1 - 31 | PV 3.00
4x0247 | Year channel 3 stop hour. | 0 - 23 | PV 3.00
4x0248 | Year channel 3 stop minute. | 0 - 59 | PV 3.00
4x0249 | Year channel 4 function. | 0 - 3 | PV 3.00
4x0250 | Year channel 4 start year. | 2000 - 2099 | PV 3.00
4x0251 | Year channel 4 start month. | 1 - 12 | PV 3.00
4x0252 | Year channel 4 start date. | 1 - 31 | PV 3.00
4x0253 | Year channel 4 start hour. | 0 - 23 | PV 3.00
4x0254 | Year channel 4 start minute. | 0 - 59 | PV 3.00
4x0255 | Year channel 4 stop year. | 2000 - 2099 | PV 3.00
4x0256 | Year channel 4 stop month. | 1 - 12 | PV 3.00
4x0257 | Year channel 4 stop date. | 1 - 31 | PV 3.00
4x0258 | Year channel 4 stop hour. | 0 - 23 | PV 3.00
4x0259 | Year channel 4 stop minute. | 0 - 59 | PV 3.00
4x0260 | Year channel 5 function. | 0 - 3 | PV 3.00
4x0261 | Year channel 5 start year. | 2000 - 2099 | PV 3.00
4x0262 | Year channel 5 start month. | 1 - 12 | PV 3.00
4x0263 | Year channel 5 start date. | 1 - 31 | PV 3.00
4x0264 | Year channel 5 start hour. | 0 - 23 | PV 3.00
4x0265 | Year channel 5 start minute. | 0 - 59 | PV 3.00
4x0266 | Year channel 5 stop year. | 2000 - 2099 | PV 3.00
4x0267 | Year channel 5 stop month. | 1 - 12 | PV 3.00
4x0268 | Year channel 5 stop date. | 1 - 31 | PV 3.00
4x0269 | Year channel 5 stop hour. | 0 - 23 | PV 3.00
4x0270 | Year channel 5 stop minute. | 0 - 59 | PV 3.00
4x0271 | Year channel 6 function. | 0 - 3 | PV 3.00
4x0272 | Year channel 6 start year. | 2000 - 2099 | PV 3.00
4x0273 | Year channel 6 start month. | 1 - 12 | PV 3.00
4x0274 | Year channel 6 start date. | 1 - 31 | PV 3.00
4x0275 | Year channel 6 start hour. | 0 - 23 | PV 3.00
4x0276 | Year channel 6 start minute. | 0 - 59 | PV 3.00
4x0277 | Year channel 6 stop year. | 2000 - 2099 | PV 3.00
4x0278 | Year channel 6 stop month. | 1 - 12 | PV 3.00
4x0279 | Year channel 6 stop date. | 1 - 31 | PV 3.00
4x0280 | Year channel 6 stop hour. | 0 - 23 | PV 3.00
4x0281 | Year channel 6 stop minute. | 0 - 59 | PV 3.00
4x0282 | Year channel 7 function. | 0 - 3 | PV 3.00
4x0283 | Year channel 7 start year. | 2000 - 2099 | PV 3.00
4x0284 | Year channel 7 start month. | 1 - 12 | PV 3.00
4x0285 | Year channel 7 start date. | 1 - 31 | PV 3.00
4x0286 | Year channel 7 start hour. | 0 - 23 | PV 3.00
4x0287 | Year channel 7 start minute. | 0 - 59 | PV 3.00
4x0288 | Year channel 7 stop year. | 2000 - 2099 | PV 3.00
4x0289 | Year channel 7 stop month. | 1 - 12 | PV 3.00
4x0290 | Year channel 7 stop date. | 1 - 31 | PV 3.00
4x0291 | Year channel 7 stop hour. | 0 - 23 | PV 3.00
4x0292 | Year channel 7 stop minute. | 0 - 59 | PV 3.00
4x0293 | Year channel 8 function. | 0 - 3 | PV 3.00
4x0294 | Year channel 8 start year. | 2000 - 2099 | PV 3.00
4x0295 | Year channel 8 start month. | 1 - 12 | PV 3.00
4x0296 | Year channel 8 start date. | 1 - 31 | PV 3.00
4x0297 | Year channel 8 start hour. | 0 - 23 | PV 3.00
4x0298 | Year channel 8 start minute. | 0 - 59 | PV 3.00
4x0299 | Year channel 8 stop year. | 2000 - 2099 | PV 3.00
4x0300 | Year channel 8 stop month. | 1 - 12 | PV 3.00
4x0301 | Year channel 8 stop date. | 1 - 31 | PV 3.00
4x0302 | Year channel 8 stop hour. | 0 - 23 | PV 3.00
4x0303 | Year channel 8 stop minute. | 0 - 59 | PV 3.00
4x0304 | Filter select. | 0 - 3 | PV 5.00
Setting for filter select function. 0=Inactive. 1=Supply air. 2=Extract air. 3=SA+EA.
4x0305 | Pre-filter select. | 0 - 3 | PV 5.00
Setting for pre-filter select function. 0=Inactive. 1=Supply air. 2=Extract air. 3=SA+EA.
4x0306 | SA pre-filter alarm limit. | 50-300Pa | PV 5.00
Supply air pre-filter pressure alarm limit setting.
4x0307 | EA pre-filter alarm limit. | 50-300Pa | PV 5.00
Extract air pre-filter pressure alarm limit setting.
4x0308 | Pre-filter calibration mode. | 0 - 3 | PV 5.00
Setting for required filter calibration. 0=Inactive. 1=SA+EA-Filter. 2=SA-Filter. 3=EA-Filter.
4x0309 | Xzone reheat function. | 0 - 4 | PV 5.00
Setting for Xzone reheat function. 0=Inactive. 1=El. coil P/P. 2=El. coil 0-10V. 3=Water coil with FP. 4=Water coil without FP.
4x0310 | Xzone cooling function. | 0 - 5 | PV 5.00
Setting for Xzone cooling function. 0=Inactive. 1=0-10V. 2=10-0V. 3=On/off 1. 4=On/off 2. 5=On/off 3.
4x0311 | Xzone temperature reg. Neutral zone. | 0.50-10.00°C | PV 5.00
Xzone neutral zone setting before shift between heating and cooling.
4x0312 | Xzone temperature regulation mode. | 0 - 3 | PV 5.00
Setting of Xzone temperature regulation type. 0=ERS 1 reg. 1=ERS 2 reg. 2=SA reg. 3=EA/Room reg.
4x0313 | Xzone ERS Step. | 1 - 4 | PV 5.00
Setting of Xzone curve when temperature is above breakpoint.
4x0314 | Xzone ERS 1 Diff. | 1.00 - 7.00°C | PV 5.00
Supply air temperature difference setting according to the diagram for Xzone ERS 1.
4x0315 | Xzone ERS 1 Breakpoint. | 12.00 - 26.00°C | PV 5.00
Breakpoint setting according to the diagram for Xzone ERS 1.
4x0316 | Xzone ERS 2 Breakpoint X1. | 10.00-38.00°C | PV 5.00
Breakpoint X1 setting according to the diagram for Xzone ERS 2.
4x0317 | Xzone ERS 2 Breakpoint Y1. | 10.00-40.00°C | PV 5.00
Breakpoint Y1 setting according to the diagram for Xzone ERS 2.
4x0318 | Xzone ERS 2 Breakpoint X2. | 11.00-39.00°C | PV 5.00
Breakpoint X2 setting according to the diagram for Xzone ERS 2.
4x0319 | Xzone ERS 2 Breakpoint Y2. | 10.00-40.00°C | PV 5.00
Breakpoint Y2 setting according to the diagram for Xzone ERS 2.
4x0320 | Xzone ERS 2 Breakpoint X3. | 12.00-40.00°C | PV 5.00
Breakpoint X3 setting according to the diagram for Xzone ERS 2.
4x0321 | Xzone ERS 2 Breakpoint Y3. | 10.00-40.00°C | PV 5.00
Breakpoint Y3 setting according to the diagram for Xzone ERS 2.
4x0322 | Xzone SA Temperature setpoint. | 10.00-40.00°C | PV 5.00
Xzone supply air temperature setting, for supply air temp regulation mode.
4x0323 | Xzone EA/Room Temperature setpoint. | 10.00-40.00°C | PV 5.00
Xzone extract air/room temperature setting, for extract air/room temp regulation mode.
4x0324 | Xzone SA Min temp setpoint. | 8.00-20.00°C | PV 5.00
Xzone supply air min.setpoint during EA/room regulation mode.
4x0325 | Xzone SA Max temp setpoint. | 16.00-50.00°C | PV 5.00
Xzone supply air max.setpoint during EA/room regulation mode.
4x0326 | Pre-heating function. | 0 - 4 | PV 5.00
Setting of pre-heating function. 0=Inactive. 1=El. coil P/P. 2=El. coil 0-10V. 3=Water coil with FP. 4=Water coil without FP.
4x0327 | Pre-heating setpoint. | -30.00-30.00°C | PV 5.00
Setting of pre-heating temperature setpoint.
4x0328 | Xzone P-band. | 1.00-40.00 | PV 5.00
Xzone regulator P-band setting.
4x0329 | Xzone SA reheat C-factor. | 0.000 - 2.500 | PV 5.00
Xzone supply air reheat regulator affection setting.
4x0330 | Xzone SA cooling C-factor. | 0.000 - 2.500 | PV 5.00
Xzone supply air cooling regulator affection setting.
4x0331 | Xzone EA reheat C-factor. | 0.000 - 2.500 | PV 5.00
Xzone extract air reheat regulator affection setting.
4x0332 | Xzone EA cooling C-factor. | 0.000 - 2.500 | PV 5.00
Xzone extract air cooling regulator affection setting.
4x0333 | Xzone SA min P-band. | 1.00 - 40.00 | PV 5.00
Xzone supply air min regulator P-band setting.
4x0334 | Xzone SA min C-factor. | 0.000 - 2.500 | PV 5.00
Xzone supply air min regulator affection setting.
4x0335 | Xzone SA max P-band. | 1.00 - 40.00 | PV 5.00
Xzone supply air max regulator P-band setting.
4x0336 | Xzone SA max C-factor. | 0.000 - 2.500 | PV 5.00
Xzone supply air min regulator affection setting.
4x0337 | Pre-heat P-band. | 1.00 - 40.00 | PV 5.00
Pre-heat regulator P-band setting.
4x0338 | Pre-heat C-factor. | 0.000 - 2.500 | PV 5.00
Pre-heat regulator affection setting.
4x0339 | ReCO2 CO2 function. | 0 - 2 | PV 5.00
Setting of ReCO2 CO2 function. 0=Inactive. 1=CO2. 2=CO2+flow.
4x0340 | ReCO2 CO2 setpoint. | 0-100.00% | PV 5.00
Setting of ReCO2 CO2 setpoint.
4x0341 | ReCO2 cooling function. | 0 - 2 | PV 5.00
Setting of ReCO2 cooling function. 0=Inactive. 1=Comfort. 2=Economy.
4x0342 | ReCO2 heating function. | 0 - 2 | PV 5.00
Setting of ReCO2 heating function. 0=Inactive. 1=Comfort. 2=Economy.
4x0343 | ReCO2 min outdoor air. | 0-8200l/s | PV 5.00
Setting of ReCO2 min outdoor air.
4x0344 | ReCO2 min exhaust air. | 0-8200l/s | PV 5.00
Setting of ReCO2 min exhaust air.
4x0345 | ReCO2 CO2 P-band. | 1.00 - 100.00 | PV 5.00
ReCO2 CO2 regulator P-band setting.
4x0346 | ReCO2 CO2 C-factor. | 0.000 - 5.000 | PV 5.00
ReCO2 CO2 regulator affection setting.
4x0347 | ReCO2 CO2 flow C-factor. | 0.000 - 5.000 | PV 5.00
ReCO2 flow regulator affection setting.
4x0348 | ReCO2 heating C-factor. | 0.000 - 5.000 | PV 5.00
ReCO2 heating regulator affection setting.
4x0349 | ReCO2 cooling C-factor. | 0.000 - 5.000 | PV 5.00
ReCO2 cooling regulator affection setting.
4x0350 | AYC function. | 0 - 3 | PV 5.07
Setting of AYC function. 0=Inactive. 1=Cool. 2=Heat. 3=Cool+heat.
4x0351 | AYC heat temp set. | 10.00-80.00°C | PV 5.07
Setting of AYC heated water temperature setpoint.
4x0352 | AYC night comp. channel. | 1 - 2 | PV 5.07
Setting of AYC night compensation channel. 1=Channel 1. 2=Channel 2.
4x0353 | AYC channel start hour. | 0-23h | PV 5.07
Setting of AYC channel start time (hour).
4x0354 | AYC channel start minute. | 0-59min | PV 5.07
Setting of AYC channel start time (minute).
4x0355 | AYC channel stop hour. | 0-23h | PV 5.07
Setting of AYC channel stop time (hour).
4x0356 | AYC channel stop minute. | 0-59min | PV 5.07
Setting of AYC channel stop time (minute).
4x0357 | AYC channel period. | 0-10 | PV 5.07
Setting of AYC channel period. 0=Inactive 1=Monday 2=Tuesday 3=Wednesday 4=Thursday 5=Friday 6=Saturday 7=Sunday 8=Monday..Friday 9=Monday..Sunday 10=Saturday..Sunday
4x0358 | AYC heat P-band. | 1.00 - 40.00 | PV 5.07
AYC heat regulator P-band setting.
4x0359 | AYC heat C-factor. | 0.000 - 2.500 | PV 5.07
AYC heat regulator affection setting.
4x0360 | AYC cool P-band. | 1.00 - 40.00 | PV 5.07
AYC cool regulator P-band setting.
4x0361 | AYC cool C-factor. | 0.000 - 2.500 | PV 5.07
AYC cool regulator affection setting.
4x0362 | AYC heat out comp. X1. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of heated water, outdoor temp X1 setting.
4x0363 | AYC heat out comp. Y1. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of heated water, heated water temp Y1 setting.
4x0364 | AYC heat out comp. X2. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of heated water, outdoor temp X2 setting.
4x0365 | AYC heat out comp. Y2. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of heated water, heated water temp Y2 setting.
4x0366 | AYC heat out comp. X3. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of heated water, outdoor temp X3 setting.
4x0367 | AYC heat out comp. Y3. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of heated water, heated water temp Y3 setting.
4x0368 | AYC heat room comp. temp limit. | 0.00-40.00°C | PV 5.07
AYC room compensation of heated water, heated water temp limit setting.
4x0369 | AYC heat room comp P-band. | 1.00-10.00°C | PV 5.07
AYC room compensation of heated water, heated water P-band setting.
4x0370 | AYC heat night comp temp. | -10.00-10.00°C | PV 5.07
AYC night compensation of heated water, heated water night setting.
4x0371 | AYC heat pump on temp. | -40.00-40.00°C | PV 5.07
AYC pump operation of heated water, outdoor temp start setting.
4x0372 | AYC heat pump off temp. | -40.00-40.00°C | PV 5.07
AYC pump operation of heated water, outdoor temp stop setting.
4x0373 | AYC heat pump alarm. | 0 - 3 | PV 5.07
Setting for selecting the AYC heated water pump alarm function. 0=Inactive. 1=Open. 2=Closed. 3=Contactor.
4x0374 | AYC heat per op function. | 0 - 3 | PV 5.07
Setting for selecting the AYC heated water periodic operation function. 0=Inactive. 1=Pump. 2=Pump+valve. 3=Valve.
4x0375 | AYC heat per op time. | 0-60min | PV 5.07
AYC periodic operation of heated water, time (minute) setting.
4x0376 | AYC heat per op interval. | 0-168h | PV 5.07
AYC periodic operation of heated water, interval time (hour) setting.
4x0377 | AYC cool out comp. X1. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of chilled water, outdoor temp X1 setting.
4x0378 | AYC cool out comp. Y1. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of chilled water, chilled water temp Y1 setting.
4x0379 | AYC cool out comp. X2. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of chilled water, outdoor temp X2 setting.
4x0380 | AYC cool out comp. Y2. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of chilled water, chilled water temp Y2 setting.
4x0381 | AYC cool out comp. X3. | -40.00-40.00°C | PV 5.07
AYC outdoor compensation of chilled water, outdoor temp X3 setting.
4x0382 | AYC cool out comp. Y3. | 10.00-80.00°C | PV 5.07
AYC outdoor compensation of chilled water, chilled water temp Y3 setting.
4x0383 | AYC cool room comp. temp limit. | 0.00-40.00°C | PV 5.07
AYC room compensation of chilled water, chilled water temp limit setting.
4x0384 | AYC cool room comp. P-band. | 1.00-10.00°C | PV 5.07
AYC room compensation of chilled water, chilled water P-band setting.
4x0385 | AYC cool night comp temp. | -10.00-10.00°C | PV 5.07
AYC night compensation of chilled water, chilled water night setting.
4x0386 | AYC cool pump on temp. | -40.00-40.00°C | PV 5.07
AYC pump operation of chilled water, outdoor temp start setting.
4x0387 | AYC cool pump off temp. | -40.00-40.00°C | PV 5.07
AYC pump operation of chilled water, outdoor temp stop setting.
4x0388 | AYC cool pump alarm. | 0 - 3 | PV 5.07
Setting for selecting the AYC chilled water pump alarm function. 0=Inactive. 1=Open. 2=Closed. 3=Contactor.
4x0389 | AYC cool per op function. | 0 - 3 | PV 5.07
Setting for selecting the AYC chilled water periodic operation function. 0=Inactive. 1=Pump. 2=Pump+valve. 3=Valve.
4x0390 | AYC cool per op time. | 0-60min | PV 5.07
AYC periodic operation of chilled water, time (minute) setting.
4x0391 | AYC cool per op interval. | 0-168h | PV 5.07
AYC periodic operation of chilled water, interval time (hour) setting.
4x0392 | IO-mod 3 output 1 function. | 0 - 10 | PV 5.07
Setting of I/O-module no. 3 relay 1 output. 0=Cooling boost. 1=Heating boost. 2=Cooling. 3=Heat exchange. 4=Reheat. 5=Down regulation. 6=Effect reduction. 7=Intermittent night heat. 8=Summer night cooling. 9=Morning boost. 10=Heat exchange defrost.
4x0393 | IO-mod 3 output 2 function. | 0 - 10 | PV 5.07
Setting of I/O-module no. 3 relay 2 output. 0=Cooling boost. 1=Heating boost. 2=Cooling. 3=Heat exchange. 4=Reheat. 5=Down regulation. 6=Effect reduction. 7=Intermittent night heat. 8=Summer night cooling. 9=Morning boost. 10=Heat exchange defrost.
4x0394 | Humid reg. func. | 0 - 3 | PV 6.07
Setting for selecting humidifying function. 0=Inactive. 1=Supply air. 2=Extract air. 3=Steam (New in PV 6.07)
4x0395 | Humid reg. Start. | 10.00-90.00% | PV 5.10
Humidifying start limit setting.
4x0396 | Humid reg. Stop. | 15.00-95.00% | PV 5.10
Humidifying stop limit setting.
4x0397 | Min/Max/Average Sens Number | 1 - 4 | PV 5.15
Setting for selecting numbers of sensors to the Min/Max/Average function.
4x0398 | Min/Max/Average Sens Function | 0 - 2 | PV 5.15
Setting for selecting sensor function. 0=Min. 1=Max. 2=Average.
4x0399 | Miru 1 Low speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 1 airflow setpoint for the unit when running in low speed operation.
4x0400 | Miru 1 High speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 1 airflow setpoint for the unit when running in high speed operation.
4x0401 | Miru 1 Low speed pressure setpoint | 0-750Pa | PV 6.04
Miru 1 air duct pressure setpoint for the unit when running in low speed operation.
4x0402 | Miru 1 High speed pressure setpoint | 0-750Pa | PV 6.04
Miru 1 air duct pressure setpoint for the unit when running in high speed operation.
4x0403 | Miru 2 Low speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 2 airflow setpoint for the unit when running in low speed operation.
4x0404 | Miru 2 High speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 2 airflow setpoint for the unit when running in high speed operation.
4x0405 | Miru 2 Low speed pressure setpoint | 0-750Pa | PV 6.04
Miru 2 air duct pressure setpoint for the unit when running in low speed operation.
4x0406 | Miru 2 High speed pressure setpoint | 0-750Pa | PV 6.04
Miru 2 air duct pressure setpoint for the unit when running in high speed operation.
4x0407 | Miru 3 Low speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 3 airflow setpoint for the unit when running in low speed operation.
4x0408 | Miru 3 High speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 3 airflow setpoint for the unit when running in high speed operation.
4x0409 | Miru 3 Low speed pressure setpoint | 0-750Pa | PV 6.04
Miru 3 air duct pressure setpoint for the unit when running in low speed operation.
4x0410 | Miru 3 High speed pressure setpoint | 0-750Pa | PV 6.04
Miru 3 air duct pressure setpoint for the unit when running in high speed operation.
4x0411 | Miru 4 Low speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 4 airflow setpoint for the unit when running in low speed operation.
4x0412 | Miru 4 High speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 4 airflow setpoint for the unit when running in high speed operation.
4x0413 | Miru 4 Low speed pressure setpoint | 0-750Pa | PV 6.04
Miru 4 air duct pressure setpoint for the unit when running in low speed operation.
4x0414 | Miru 4 High speed pressure setpoint | 0-750Pa | PV 6.04
Miru 4 air duct pressure setpoint for the unit when running in high speed operation.
4x0415 | Miru 5 Low speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 5 airflow setpoint for the unit when running in low speed operation.
4x0416 | Miru 5 High speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 5 airflow setpoint for the unit when running in high speed operation.
4x0417 | Miru 5 Low speed pressure setpoint | 0-750Pa | PV 6.04
Miru 5 air duct pressure setpoint for the unit when running in low speed operation.
4x0418 | Miru 5 High speed pressure setpoint | 0-750Pa | PV 6.04
Miru 5 air duct pressure setpoint for the unit when running in high speed operation.
4x0419 | Miru 6 Low speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 6 airflow setpoint for the unit when running in low speed operation.
4x0420 | Miru 6 High speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 6 airflow setpoint for the unit when running in high speed operation.
4x0421 | Miru 6 Low speed pressure setpoint | 0-750Pa | PV 6.04
Miru 6 air duct pressure setpoint for the unit when running in low speed operation.
4x0422 | Miru 6 High speed pressure setpoint | 0-750Pa | PV 6.04
Miru 6 air duct pressure setpoint for the unit when running in high speed operation.
4x0423 | Miru 7 Low speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 7 airflow setpoint for the unit when running in low speed operation.
4x0424 | Miru 7 High speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 7 airflow setpoint for the unit when running in high speed operation.
4x0425 | Miru 7 Low speed pressure setpoint | 0-750Pa | PV 6.04
Miru 7 air duct pressure setpoint for the unit when running in low speed operation.
4x0426 | Miru 7 High speed pressure setpoint | 0-750Pa | PV 6.04
Miru 7 air duct pressure setpoint for the unit when running in high speed operation.
4x0427 | Miru 8 Low speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 8 airflow setpoint for the unit when running in low speed operation.
4x0428 | Miru 8 High speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 8 airflow setpoint for the unit when running in high speed operation.
4x0429 | Miru 8 Low speed pressure setpoint | 0-750Pa | PV 6.04
Miru 8 air duct pressure setpoint for the unit when running in low speed operation.
4x0430 | Miru 8 High speed pressure setpoint | 0-750Pa | PV 6.04
Miru 8 air duct pressure setpoint for the unit when running in high speed operation.
4x0431 | Miru 9 Low speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 9 airflow setpoint for the unit when running in low speed operation.
4x0432 | Miru 9 High speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 9 airflow setpoint for the unit when running in high speed operation.
4x0433 | Miru 9 Low speed pressure setpoint | 0-750Pa | PV 6.04
Miru 9 air duct pressure setpoint for the unit when running in low speed operation.
4x0434 | Miru 9 High speed pressure setpoint | 0-750Pa | PV 6.04
Miru 9 air duct pressure setpoint for the unit when running in high speed operation.
4x0435 | Miru 10 Low speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 10 airflow setpoint for the unit when running in low speed operation.
4x0436 | Miru 10 High speed airflow setpoint | 0-10000l/s | PV 6.04
Miru 10 airflow setpoint for the unit when running in high speed operation.
4x0437 | Miru 10 Low speed pressure setpoint | 0-750Pa | PV 6.04
Miru 10 air duct pressure setpoint for the unit when running in low speed operation.
4x0438 | Miru 10 High speed pressure setpoint | 0-750Pa | PV 6.04
Miru 10 air duct pressure setpoint for the unit when running in high speed operation.
4x0439 | BB Cool temp setpoint | -20.0-80.0°C | PV 6.05
Blue Box cooling temperature setpoint.
4x0440 | BB Heat temp setpoint | 10.0-80.0°C | PV 6.05
Blue Box heating temperature setpoint.
4x0441 | BB Unit type | 0-3 | PV 6.05
Blue Box unit type. 0=None 1=Heat pump 2=Chiller 3=Reversible
4x0442 | BB Optimize upper valve limit | 70.00-100.00% | PV 6.05
Blue Box optimize function upper valve limit.
4x0443 | BB Optimize lower valve limit | 5.00-90.00% | PV 6.05
Blue Box optimize function lower valve limit.
4x0444 | BB Optimize delay | 30-32000s | PV 6.05
Blue Box optimize function delay time.
4x0445 | BB Cool optimize up | 0.1-6.0°C | PV 6.05
Blue Box cooling optimize function up.
4x0446 | BB Cool optimize down | 0.1-6.0°C | PV 6.05
Blue Box cooling optimize function down.
4x0447 | BB Heat optimize up | 0.1-6.0°C | PV 6.05
Blue Box heating optimize function up.
4x0448 | BB Heat optimize down | 0.1-6.0°C | PV 6.05
Blue Box heating optimize function down.
4x0449 | BB Cool optimize diff temperature | 1.0-10.0°C | PV 6.05
Blue Box cooling optimize function differential temperature.
4x0450 | BB Heat optimize diff temperature | 1.0-10.0°C | PV 6.05
Blue Box heating optimize function differential temperature.
4x0451 | BB AQUA Link function | 0-3 | PV 6.05
Blue Box AQUA Link function. 0=Inactive 1=Heat 2=Cool 3=Heat + Cool
4x0452 | BB AQUA Link cool pump alarm function | 0-3 | PV 6.05
Blue Box AQUA Link cool pump alarm function. 0=Inactive 1=Open 2=Close 3=Contactor
4x0453 | BB AQUA Link heat pump alarm function | 0-3 | PV 6.05
Blue Box AQUA Link heat pump alarm function. 0=Inactive 1=Open 2=Close 3=Contactor
4x0454 | Extended ext. reg. seq. reheat function | 0-4 | PV 6.07
Extended extra regulation sequence reheat function. 0=Inactive 1=El. P/P 2=El. 0-10V 3=Water FP 4=Water
4x0455 | Season heat mode setpoint | 0-2 | PV 6.07
Season heat mode type setpoint. 0=Digital Input NO 1=Digital Input NC 2=Manual
4x0456 | Season heat function | 0-1 | PV 6.07
Season heating function. 0=Inactive 1=Active
4x0457 | Steam humid extract air setpoint | 0-100.00% | PV 6.07
Steam humidification extract air setpoint.
4x0458 | Steam humid supply air max limit | 0-100.00% | PV 6.07
Steam humidification supply air max limit.
4x0459 | Steam humid extract air P-band | 1-60.00% | PV 6.07
Steam humidification extract air P-band.
4x0460 | Steam humid extract air C-factor | 0-3.000 | PV 6.07
Steam humidification extract air C-factor.
4x0461 | Steam humid supply air max P-band | 1-60.00% | PV 6.07
Steam humidification supply air max P-band.
4x0462 | Steam humid supply air max C-factor | 0-3.000 | PV 6.07
Steam humidification supply air max C-factor.
4x0463 | End-filter alarm limit | 10-1000Pa | PV 6.07
Supply air end-filter pressure alarm limit setting.
4x0464 | End-filter select | 0-1 | PV 6.07
Supply air end-filter function. 0=Inactive. 1=Active
4x0465 | End-filter calibration | 0-1 | PV 6.07
Supply air end-filter calibration. 0=Inactive 1=Active